## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 0 | 1 | 2 | 16 | 29.4 | 25.82 | 50 | 92.1 | 44.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 0 | 34 | 34 | 3 | 70.9 | 9.78 | 50 | 92.1 | 44.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 1 | 2 | 2 | 16 | 29.4 | 25.01 | 50 | 92.1 | 44.7 | 33.3 | 76.9 | 223.8 | 195.5 | 195.5 | NO
1 | OK | 34 | 29 | 29 | 3 | 98.2 | 9.78 | 50 | 92.1 | 44.7 | 69.5 | 56.6 | 216.1 | 214 | 214 | YES
| NG | 2 | 3 | 9 | 55 | 39.8 | 23.57 | 50 | 92.1 | 44.7 | 36.6 | 53.1 | 223.8 | 203.6 | 203.6 | NO
2 | OK | 29 | 30 | 30 | 3 | 123.3 | 8.27 | 50 | 92.1 | 44.7 | 72.9 | 54.7 | 215.9 | 214.5 | 214.5 | YES
| NG | 3 | 18 | 9 | 55 | 39.8 | 16.17 | 50 | 92.1 | 44.7 | 53.9 | 53.1 | 219 | 203.6 | 203.6 | NO
3 | ** OPTIMAL ** | 30 | 31 | 31 | 3 | 146.4 | 8.27 | 50 | 92.1 | 44.7 | 72.9 | 54.7 | 215.9 | 214.5 | 214.5 | YES
| NG | 18 | 28 | 9 | 55 | 39.8 | 13.41 | 50 | 92.1 | 44.7 | 60.4 | 53.1 | 217.7 | 203.6 | 203.6 | NO
| NG | 28 | 27 | 9 | 55 | 39.8 | 12.04 | 50 | 92.1 | 44.7 | 63.7 | 53.1 | 216.1 | 203.6 | 203.6 | NO
| NG | 27 | 16 | 9 | 55 | 39.8 | 10.74 | 50 | 92.1 | 44.7 | 66.8 | 53.1 | 214.5 | 203.6 | 203.6 | NO
| NG | 16 | 14 | 9 | 55 | 39.8 | 9.49 | 50 | 92.1 | 44.7 | 69.9 | 53.1 | 212.5 | 203.6 | 203.6 | NO
| NG | 14 | 13 | 9 | 55 | 39.8 | 8.94 | 50 | 92.1 | 44.7 | 71.2 | 51.1 | 212.6 | 208.7 | 208.7 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 54-007281
TR_B (available) | 59-000574
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 92.1
TR_B Baseline Loading% | 44.7
Total Scenarios Evaluated | 13
Feasible Scenarios | 3
--- Optimal Solution ---
Switch Parent Node | 30
Switch Child Node | 31
Tie Node (TR_A side) | 31
Tie Node (TR_B side) | 3
Tie Line Distance (m) | 146.4
Load Transferred (kW) | 8.27
TR_A Loading After (%) | 72.9
TR_B Loading After (%) | 54.7
Minimum Voltage (V) | 214.5