## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 0 | 1 | 18 | 3 | 31.8 | 25.82 | 50 | 92.1 | 11.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 0 | 34 | 34 | 3 | 3.3 | 9.78 | 50 | 92.1 | 11.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 1 | 2 | 18 | 3 | 31.8 | 25.01 | 50 | 92.1 | 11.8 | 33.3 | 71 | 223.8 | 214.2 | 214.2 | YES
2 | OK | 34 | 29 | 29 | 3 | 28.1 | 9.78 | 50 | 92.1 | 11.8 | 69.5 | 34.5 | 216.1 | 223 | 216.1 | YES
3 | OK | 2 | 3 | 18 | 3 | 31.8 | 23.57 | 50 | 92.1 | 11.8 | 36.6 | 67.6 | 223.8 | 214.1 | 214.1 | YES
4 | OK | 29 | 30 | 30 | 3 | 53.1 | 8.27 | 50 | 92.1 | 11.8 | 72.9 | 31 | 215.9 | 223.4 | 215.9 | YES
5 | ** OPTIMAL ** | 3 | 18 | 18 | 3 | 31.8 | 16.17 | 50 | 92.1 | 11.8 | 53.9 | 49.7 | 219 | 219.6 | 219 | YES
6 | OK | 30 | 31 | 31 | 3 | 76.1 | 8.27 | 50 | 92.1 | 11.8 | 72.9 | 31 | 215.9 | 223.4 | 215.9 | YES
7 | OK | 18 | 28 | 28 | 3 | 36 | 13.41 | 50 | 92.1 | 11.8 | 60.4 | 43.2 | 217.7 | 219.2 | 217.7 | YES
8 | OK | 31 | 32 | 32 | 3 | 128.2 | 6.51 | 50 | 92.1 | 11.8 | 77 | 26.9 | 215.9 | 223 | 215.9 | YES
9 | OK | 28 | 27 | 27 | 3 | 71.1 | 12.04 | 50 | 92.1 | 11.8 | 63.7 | 40 | 216.1 | 219.2 | 216.1 | YES
10 | OK | 27 | 16 | 16 | 3 | 105.5 | 10.74 | 50 | 92.1 | 11.8 | 66.8 | 37 | 214.5 | 219.1 | 214.5 | YES
11 | OK | 16 | 14 | 14 | 3 | 150.1 | 9.49 | 50 | 92.1 | 11.8 | 69.9 | 34.2 | 212.5 | 219 | 212.5 | YES
12 | OK | 14 | 13 | 15 | 3 | 159.1 | 8.94 | 50 | 92.1 | 11.8 | 71.2 | 30.6 | 212.6 | 221.5 | 212.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 54-007281
TR_B (available) | 67-013159
TR_A Rated kVA | 50
TR_B Rated kVA | 50
TR_A Baseline Loading% | 92.1
TR_B Baseline Loading% | 11.8
Total Scenarios Evaluated | 14
Feasible Scenarios | 12
--- Optimal Solution ---
Switch Parent Node | 3
Switch Child Node | 18
Tie Node (TR_A side) | 18
Tie Node (TR_B side) | 3
Tie Line Distance (m) | 31.8
Load Transferred (kW) | 16.17
TR_A Loading After (%) | 53.9
TR_B Loading After (%) | 49.7
Minimum Voltage (V) | 219