## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 26 | 41 | 35 | 27 | 2.4 | 6.95 | 50 | 60.7 | 32.9 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 41 | 43 | 35 | 27 | 2.4 | 6.95 | 50 | 60.7 | 32.9 | 44.3 | 40.9 | 219 | 221.8 | 219 | YES
2 | ** OPTIMAL ** | 43 | 44 | 35 | 27 | 2.4 | 5.84 | 50 | 60.7 | 32.9 | 46.8 | 39.5 | 219 | 223 | 219 | YES
3 | OK | 44 | 27 | 35 | 27 | 2.4 | 5.53 | 50 | 60.7 | 32.9 | 47.5 | 39.4 | 218.9 | 223.1 | 218.9 | YES
4 | OK | 27 | 28 | 35 | 27 | 2.4 | 4.83 | 50 | 60.7 | 32.9 | 49.1 | 38.6 | 218.9 | 224 | 218.9 | YES
5 | OK | 27 | 36 | 30 | 50 | 63.4 | 0.7 | 50 | 60.7 | 32.9 | 59 | 33.8 | 217.1 | 223.6 | 217.1 | YES
6 | OK | 28 | 3 | 35 | 27 | 2.4 | 3.8 | 50 | 60.7 | 32.9 | 51.5 | 37.4 | 218.9 | 223.9 | 218.9 | YES
7 | OK | 36 | 37 | 30 | 50 | 63.4 | 0.7 | 50 | 60.7 | 32.9 | 59 | 33.8 | 217.1 | 223.6 | 217.1 | YES
8 | OK | 3 | 4 | 35 | 27 | 2.4 | 3.02 | 50 | 60.7 | 32.9 | 53.4 | 36.2 | 218.9 | 223.8 | 218.9 | YES
9 | OK | 37 | 29 | 30 | 50 | 63.4 | 0.66 | 50 | 60.7 | 32.9 | 59.1 | 33.7 | 217 | 223.6 | 217 | YES
10 | OK | 4 | 33 | 33 | 27 | 31.9 | 1.3 | 50 | 60.7 | 32.9 | 57.5 | 34.4 | 218.6 | 223.7 | 218.6 | YES
11 | OK | 4 | 34 | 35 | 27 | 2.4 | 1.25 | 50 | 60.7 | 32.9 | 57.6 | 34.4 | 218.6 | 223.7 | 218.6 | YES
12 | OK | 4 | 32 | 32 | 27 | 34.1 | 0.25 | 50 | 60.7 | 32.9 | 60.1 | 33.2 | 216.2 | 223.6 | 216.2 | YES
13 | OK | 34 | 35 | 35 | 27 | 2.4 | 1.25 | 50 | 60.7 | 32.9 | 57.6 | 32.9 | 218.6 | 223.6 | 218.6 | YES
14 | OK | 32 | 31 | 31 | 20 | 35.4 | 0.15 | 50 | 60.7 | 32.9 | 60.3 | 33.1 | 215.9 | 223.6 | 215.9 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 54-011063
TR_B (available) | 60-023863
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 60.7
TR_B Baseline Loading% | 32.9
Total Scenarios Evaluated | 15
Feasible Scenarios | 14
--- Optimal Solution ---
Switch Parent Node | 43
Switch Child Node | 44
Tie Node (TR_A side) | 35
Tie Node (TR_B side) | 27
Tie Line Distance (m) | 2.4
Load Transferred (kW) | 5.84
TR_A Loading After (%) | 46.8
TR_B Loading After (%) | 39.5
Minimum Voltage (V) | 219