## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 26 | 24 | 6 | 9 | 117.5 | 18.95 | 50 | 60.7 | 29.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 24 | 62 | 6 | 9 | 117.5 | 17.16 | 50 | 60.7 | 29.8 | 20.5 | 43.5 | 217.6 | 206.5 | 206.5 | NO
| NG | 62 | 64 | 6 | 9 | 117.5 | 16.93 | 50 | 60.7 | 29.8 | 21.1 | 43.2 | 217.5 | 206.2 | 206.2 | NO
1 | OK | 64 | 20 | 6 | 9 | 117.5 | 12 | 50 | 60.7 | 29.8 | 32.4 | 37.1 | 216 | 212.2 | 212.2 | YES
2 | OK | 20 | 21 | 6 | 9 | 117.5 | 11.61 | 50 | 60.7 | 29.8 | 33.3 | 36.6 | 216 | 213.4 | 213.4 | YES
3 | OK | 21 | 22 | 6 | 9 | 117.5 | 10.45 | 50 | 60.7 | 29.8 | 36 | 35.1 | 216 | 218 | 216 | YES
4 | OK | 22 | 19 | 6 | 9 | 117.5 | 9.37 | 50 | 60.7 | 29.8 | 38.5 | 33.8 | 216 | 217.6 | 216 | YES
5 | OK | 19 | 11 | 6 | 9 | 117.5 | 9.37 | 50 | 60.7 | 29.8 | 38.5 | 33.8 | 216 | 217.6 | 216 | YES
| NG | 11 | 10 | 53 | 46 | 151.2 | 5.9 | 50 | 60.7 | 29.8 | 46.8 | 37.2 | 215.6 | 207.6 | 207.6 | NO
6 | ** OPTIMAL ** | 11 | 9 | 6 | 9 | 117.5 | 3.47 | 50 | 60.7 | 29.8 | 52.5 | 33.8 | 216 | 217.6 | 216 | YES
| NG | 10 | 12 | 53 | 46 | 151.2 | 5.81 | 50 | 60.7 | 29.8 | 47 | 37.1 | 215.6 | 208 | 208 | NO
7 | OK | 9 | 8 | 6 | 9 | 117.5 | 2.66 | 50 | 60.7 | 29.8 | 54.4 | 32.9 | 215.6 | 217.6 | 215.6 | YES
8 | OK | 12 | 13 | 53 | 46 | 151.2 | 4.25 | 50 | 60.7 | 29.8 | 50.6 | 35 | 215.6 | 214.2 | 214.2 | YES
9 | OK | 8 | 7 | 6 | 9 | 117.5 | 1.19 | 50 | 60.7 | 29.8 | 57.9 | 31.1 | 215.6 | 216.8 | 215.6 | YES
10 | OK | 13 | 40 | 53 | 46 | 151.2 | 4.23 | 50 | 60.7 | 29.8 | 50.6 | 35 | 215.6 | 214.3 | 214.3 | YES
11 | OK | 7 | 5 | 6 | 9 | 117.5 | 0.96 | 50 | 60.7 | 29.8 | 58.4 | 30.9 | 215.6 | 216.7 | 215.6 | YES
12 | OK | 40 | 16 | 53 | 46 | 151.2 | 3.52 | 50 | 60.7 | 29.8 | 52.3 | 34 | 215.6 | 216.2 | 215.6 | YES
13 | OK | 5 | 6 | 6 | 9 | 117.5 | 0.51 | 50 | 60.7 | 29.8 | 59.5 | 29.9 | 215.6 | 216.3 | 215.6 | YES
14 | OK | 16 | 17 | 53 | 46 | 151.2 | 1.82 | 50 | 60.7 | 29.8 | 56.3 | 30.7 | 215.6 | 216.2 | 215.6 | YES
15 | OK | 17 | 53 | 53 | 46 | 151.2 | 0.8 | 50 | 60.7 | 29.8 | 58.7 | 30.7 | 215.6 | 216.2 | 215.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 54-011063
TR_B (available) | 62-005397
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 60.7
TR_B Baseline Loading% | 29.8
Total Scenarios Evaluated | 20
Feasible Scenarios | 15
--- Optimal Solution ---
Switch Parent Node | 11
Switch Child Node | 9
Tie Node (TR_A side) | 6
Tie Node (TR_B side) | 9
Tie Line Distance (m) | 117.5
Load Transferred (kW) | 3.47
TR_A Loading After (%) | 52.5
TR_B Loading After (%) | 33.8
Minimum Voltage (V) | 216