## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 26 | 24 | 61 | 0 | 141 | 18.95 | 50 | 60.7 | 3.4 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | ** OPTIMAL ** | 24 | 23 | 61 | 0 | 141 | 1.65 | 50 | 60.7 | 3.4 | 56.9 | 9.9 | 216.4 | 221.9 | 216.4 | YES
2 | OK | 23 | 25 | 61 | 0 | 141 | 1.2 | 50 | 60.7 | 3.4 | 58 | 8.1 | 216.2 | 224.5 | 216.2 | YES
| NG | 25 | 49 | 61 | 0 | 141 | 1.2 | 50 | 60.7 | 3.4 | 58 |  | 216.2 | 8.7794e+67 | 216.2 | NO
3 | OK | 49 | 39 | 61 | 0 | 141 | 1.13 | 50 | 60.7 | 3.4 | 58.1 | 7.8 | 216.2 | 224.8 | 216.2 | YES
4 | OK | 39 | 38 | 61 | 0 | 141 | 1.13 | 50 | 60.7 | 3.4 | 58.1 | 7.8 | 216.2 | 224.8 | 216.2 | YES
5 | OK | 38 | 63 | 61 | 0 | 141 | 0.48 | 50 | 60.7 | 3.4 | 59.6 | 5.3 | 215.8 | 228.1 | 215.8 | YES
6 | OK | 63 | 2 | 61 | 0 | 141 | 0.45 | 50 | 60.7 | 3.4 | 59.7 | 5.2 | 215.8 | 228.3 | 215.8 | YES
7 | OK | 2 | 52 | 61 | 0 | 141 | 0.32 | 50 | 60.7 | 3.4 | 60 | 4.7 | 215.7 | 228.9 | 215.7 | YES
8 | OK | 52 | 45 | 61 | 0 | 141 | 0.32 | 50 | 60.7 | 3.4 | 60 | 4.7 | 215.7 | 228.9 | 215.7 | YES
9 | OK | 45 | 46 | 61 | 0 | 141 | 0.26 | 50 | 60.7 | 3.4 | 60.1 | 4.4 | 215.7 | 229.2 | 215.7 | YES
10 | OK | 46 | 50 | 61 | 0 | 141 | 0.26 | 50 | 60.7 | 3.4 | 60.1 | 3.9 | 215.7 | 229.8 | 215.7 | YES
11 | OK | 50 | 55 | 61 | 0 | 141 | 0.01 | 50 | 60.7 | 3.4 | 60.7 | 3.5 | 215.6 | 230.2 | 215.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 54-011063
TR_B (available) | 68-008005
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 60.7
TR_B Baseline Loading% | 3.4
Total Scenarios Evaluated | 13
Feasible Scenarios | 11
--- Optimal Solution ---
Switch Parent Node | 24
Switch Child Node | 23
Tie Node (TR_A side) | 61
Tie Node (TR_B side) | 0
Tie Line Distance (m) | 141
Load Transferred (kW) | 1.65
TR_A Loading After (%) | 56.9
TR_B Loading After (%) | 9.9
Minimum Voltage (V) | 216.4