## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 2 | 69 | 123 | 57 | 122.8 | 19.94 | 50 | 78.3 | 49.6 | [5 empty] | NO | TR_B sim: not converged
| NG | 69 | 116 | 123 | 57 | 122.8 | 10.23 | 50 | 78.3 | 49.6 | 66.2 | 56.6 | 204 | 187.2 | 187.2 | NO
| NG | 116 | 16 | 123 | 57 | 122.8 | 10.23 | 50 | 78.3 | 49.6 | 66.2 | 56.6 | 204 | 187.2 | 187.2 | NO
| NG | 21 | 20 | 57 | 24 | 73.1 | 30.14 | 50 | 78.3 | 49.6 | 42.1 | 70.9 | 220.4 | 159.8 | 159.8 | NO
| NG | 16 | 17 | 146 | 4 | 227.6 | 6.83 | 50 | 78.3 | 49.6 | 70.3 | 56.1 | 204 | 201.7 | 201.7 | NO
| NG | 20 | 67 | 57 | 24 | 73.1 | 28.14 | 50 | 78.3 | 49.6 | 44.4 | 70.9 | 220.4 | 159.8 | 159.8 | NO
| NG | 17 | 120 | 146 | 4 | 227.6 | 6.51 | 50 | 78.3 | 49.6 | 70.6 | 56.1 | 204 | 201.7 | 201.7 | NO
| NG | 67 | 66 | 57 | 24 | 73.1 | 27.28 | 50 | 78.3 | 49.6 | 45.4 | 68.9 | 220.2 | 166.5 | 166.5 | NO
| NG | 120 | 51 | 146 | 4 | 227.6 | 6.03 | 50 | 78.3 | 49.6 | 71.2 | 56.1 | 204 | 201.7 | 201.7 | NO
| NG | 66 | 45 | 57 | 24 | 73.1 | 27.14 | 50 | 78.3 | 49.6 | 45.6 | 68.9 | 220.2 | 166.5 | 166.5 | NO
| NG | 51 | 138 | 146 | 4 | 227.6 | 4.83 | 50 | 78.3 | 49.6 | 72.6 | 54.9 | 203.9 | 206.2 | 203.9 | NO
| NG | 45 | 46 | 52 | 51 | 277.8 | 3.59 | 50 | 78.3 | 49.6 | 74 | 53.8 | 203.3 | 219.8 | 203.3 | NO
| NG | 45 | 83 | 57 | 24 | 73.1 | 14.17 | 50 | 78.3 | 49.6 | 60.8 | 60.9 | 219.2 | 197.3 | 197.3 | NO
| NG | 138 | 49 | 146 | 4 | 227.6 | 4.22 | 50 | 78.3 | 49.6 | 73.3 | 54.9 | 203.8 | 206.2 | 203.8 | NO
| NG | 46 | 53 | 52 | 51 | 277.8 | 3.24 | 50 | 78.3 | 49.6 | 74.4 | 53.4 | 203 | 219.8 | 203 | NO
| NG | 83 | 82 | 57 | 24 | 73.1 | 11.81 | 50 | 78.3 | 49.6 | 63.6 | 60.9 | 219.2 | 197.3 | 197.3 | NO
| NG | 49 | 50 | 146 | 4 | 227.6 | 3.46 | 50 | 78.3 | 49.6 | 74.2 | 53.9 | 203.6 | 210 | 203.6 | NO
| NG | 53 | 54 | 52 | 51 | 277.8 | 2.16 | 50 | 78.3 | 49.6 | 75.7 | 52.1 | 203.1 | 220 | 203.1 | NO
| NG | 82 | 81 | 57 | 24 | 73.1 | 11.23 | 50 | 78.3 | 49.6 | 64.3 | 60 | 219.1 | 200 | 200 | NO
| NG | 50 | 145 | 146 | 4 | 227.6 | 2.88 | 50 | 78.3 | 49.6 | 74.8 | 53.1 | 203.5 | 212.7 | 203.5 | NO
| NG | 54 | 52 | 52 | 51 | 277.8 | 0.44 | 50 | 78.3 | 49.6 | 77.7 | 50.1 | 203.2 | 220.2 | 203.2 | NO
| NG | 81 | 77 | 57 | 24 | 73.1 | 10.13 | 50 | 78.3 | 49.6 | 65.6 | 60 | 219.1 | 200 | 200 | NO
| NG | 145 | 47 | 146 | 4 | 227.6 | 2.39 | 50 | 78.3 | 49.6 | 75.4 | 52.5 | 203.4 | 214.9 | 203.4 | NO
| NG | 77 | 59 | 57 | 24 | 73.1 | 9.26 | 50 | 78.3 | 49.6 | 66.6 | 60 | 219.1 | 200 | 200 | NO
| NG | 47 | 48 | 146 | 4 | 227.6 | 1.15 | 50 | 78.3 | 49.6 | 76.9 | 51 | 203.1 | 220.1 | 203.1 | NO
| NG | 59 | 43 | 57 | 24 | 73.1 | 8.12 | 50 | 78.3 | 49.6 | 68 | 58.4 | 218.8 | 204.8 | 204.8 | NO
| NG | 43 | 44 | 42 | 48 | 224.5 | 0.29 | 50 | 78.3 | 49.6 | 77.9 | 49.9 | 203.3 | 220.2 | 203.3 | NO
| NG | 43 | 56 | 57 | 24 | 73.1 | 6.66 | 50 | 78.3 | 49.6 | 69.7 | 58 | 218.8 | 206.1 | 206.1 | NO
| NG | 44 | 42 | 42 | 48 | 224.5 | 0.05 | 50 | 78.3 | 49.6 | 78.2 | 49.6 | 202.9 | 220.2 | 202.9 | NO
| NG | 56 | 55 | 57 | 24 | 73.1 | 5.82 | 50 | 78.3 | 49.6 | 70.7 | 56.8 | 218 | 209.2 | 209.2 | NO
| NG | 55 | 76 | 57 | 24 | 73.1 | 5.79 | 50 | 78.3 | 49.6 | 70.8 | 56.8 | 218 | 209.3 | 209.3 | NO
1 | OK | 76 | 75 | 57 | 24 | 73.1 | 4.63 | 50 | 78.3 | 49.6 | 72.2 | 55.3 | 216.3 | 212.8 | 212.8 | YES
2 | ** OPTIMAL ** | 75 | 57 | 57 | 24 | 73.1 | 4.41 | 50 | 78.3 | 49.6 | 72.4 | 55 | 215.8 | 213.4 | 213.4 | YES
| NG | 57 | 133 | 133 | 24 | 125.5 | 0.33 | 50 | 78.3 | 49.6 | 77.8 | 50 | 203.9 | 220.2 | 203.9 | NO
| NG | 133 | 136 | 136 | 24 | 184 | 0.25 | 50 | 78.3 | 49.6 | 77.9 | 49.9 | 203.6 | 220.2 | 203.6 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 54-016944
TR_B (available) | 62-003172
TR_A Rated kVA | 100
TR_B Rated kVA | 100
TR_A Baseline Loading% | 78.3
TR_B Baseline Loading% | 49.6
Total Scenarios Evaluated | 35
Feasible Scenarios | 2
--- Optimal Solution ---
Switch Parent Node | 75
Switch Child Node | 57
Tie Node (TR_A side) | 57
Tie Node (TR_B side) | 24
Tie Line Distance (m) | 73.1
Load Transferred (kW) | 4.41
TR_A Loading After (%) | 72.4
TR_B Loading After (%) | 55
Minimum Voltage (V) | 213.4