## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 21 | 22 | 14 | 3 | 8.2 | 19.54 | 50 | 84.6 | 10 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 21 | 20 | 20 | 3 | 147.6 | 2.11 | 50 | 84.6 | 10 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 22 | 30 | 14 | 3 | 8.2 | 9.7 | 50 | 84.6 | 10 | 46.4 | 47.7 | 214.6 | 216.4 | 214.6 | YES
2 | ** OPTIMAL ** | 30 | 29 | 14 | 3 | 8.2 | 9.7 | 50 | 84.6 | 10 | 46.4 | 47.7 | 214.6 | 216.4 | 214.6 | YES
3 | OK | 29 | 28 | 14 | 3 | 8.2 | 9.69 | 50 | 84.6 | 10 | 46.5 | 47.6 | 214.5 | 216.4 | 214.5 | YES
4 | OK | 28 | 5 | 14 | 3 | 8.2 | 9.69 | 50 | 84.6 | 10 | 46.5 | 47.6 | 214.5 | 216.4 | 214.5 | YES
| NG | 5 | 6 | 14 | 3 | 8.2 | 4.33 | 50 | 84.6 | 10 | 67.4 | 26.6 | 209.8 | 223.8 | 209.8 | NO
5 | OK | 5 | 9 | 9 | 3 | 121.2 | 5.36 | 50 | 84.6 | 10 | 63.4 | 30.7 | 210.7 | 221.2 | 210.7 | YES
| NG | 6 | 35 | 14 | 3 | 8.2 | 4.03 | 50 | 84.6 | 10 | 68.5 | 25.5 | 209.5 | 224.1 | 209.5 | NO
| NG | 9 | 31 | 31 | 3 | 139.9 | 4.35 | 50 | 84.6 | 10 | 67.3 | 26.8 | 209.8 | 222.7 | 209.8 | NO
| NG | 35 | 15 | 14 | 3 | 8.2 | 3.83 | 50 | 84.6 | 10 | 69.3 | 24.7 | 209.3 | 224.3 | 209.3 | NO
| NG | 15 | 12 | 12 | 3 | 32 | 3.83 | 50 | 84.6 | 10 | 69.3 | 24.7 | 209.3 | 224.3 | 209.3 | NO
| NG | 12 | 13 | 13 | 3 | 54.3 | 3.54 | 50 | 84.6 | 10 | 70.5 | 23.6 | 209.1 | 224.7 | 209.1 | NO
| NG | 13 | 37 | 37 | 3 | 89.5 | 2.37 | 50 | 84.6 | 10 | 75.1 | 19.1 | 208 | 225.9 | 208 | NO
| NG | 37 | 38 | 38 | 2 | 131.5 | 2.27 | 50 | 84.6 | 10 | 75.5 | 18.7 | 207.9 | 226 | 207.9 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 54-017107
TR_B (available) | 49-010567
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 84.6
TR_B Baseline Loading% | 10
Total Scenarios Evaluated | 15
Feasible Scenarios | 5
--- Optimal Solution ---
Switch Parent Node | 30
Switch Child Node | 29
Tie Node (TR_A side) | 14
Tie Node (TR_B side) | 3
Tie Line Distance (m) | 8.2
Load Transferred (kW) | 9.7
TR_A Loading After (%) | 46.4
TR_B Loading After (%) | 47.7
Minimum Voltage (V) | 214.6