## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 45 | 7 | 47 | 3 | 121.9 | 14.14 | 50 | 80.7 | 22.6 | 25.4 | 34.2 | 216.2 | 180.5 | 180.5 | NO
| NG | 7 | 6 | 47 | 3 | 121.9 | 14.14 | 50 | 80.7 | 22.6 | 25.4 | 34.2 | 216.2 | 180.5 | 180.5 | NO
| NG | 6 | 37 | 47 | 3 | 121.9 | 13.48 | 50 | 80.7 | 22.6 | 28 | 33.4 | 215.8 | 183.6 | 183.6 | NO
| NG | 37 | 5 | 47 | 3 | 121.9 | 13.48 | 50 | 80.7 | 22.6 | 28 | 33.4 | 215.8 | 183.6 | 183.6 | NO
| NG | 5 | 4 | 47 | 3 | 121.9 | 12.28 | 50 | 80.7 | 22.6 | 32.5 | 33.4 | 215.8 | 183.6 | 183.6 | NO
1 | OK | 4 | 39 | 47 | 3 | 121.9 | 3.07 | 50 | 80.7 | 22.6 | 68.5 | 26.5 | 212.4 | 210.1 | 210.1 | YES
2 | ** OPTIMAL ** | 39 | 41 | 47 | 3 | 121.9 | 2.49 | 50 | 80.7 | 22.6 | 70.7 | 25.8 | 212 | 212.9 | 212 | YES
3 | OK | 41 | 50 | 47 | 3 | 121.9 | 1.31 | 50 | 80.7 | 22.6 | 75.4 | 24.2 | 211 | 219.4 | 211 | YES
4 | OK | 50 | 49 | 47 | 3 | 121.9 | 1.19 | 50 | 80.7 | 22.6 | 75.9 | 24.1 | 210.9 | 219.9 | 210.9 | YES
5 | OK | 49 | 2 | 47 | 3 | 121.9 | 0.72 | 50 | 80.7 | 22.6 | 77.8 | 23.5 | 210.5 | 221.9 | 210.5 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 55-001215
TR_B (available) | 59-024425
TR_A Rated kVA | 30
TR_B Rated kVA | 100
TR_A Baseline Loading% | 80.7
TR_B Baseline Loading% | 22.6
Total Scenarios Evaluated | 10
Feasible Scenarios | 5
--- Optimal Solution ---
Switch Parent Node | 39
Switch Child Node | 41
Tie Node (TR_A side) | 47
Tie Node (TR_B side) | 3
Tie Line Distance (m) | 121.9
Load Transferred (kW) | 2.49
TR_A Loading After (%) | 70.7
TR_B Loading After (%) | 25.8
Minimum Voltage (V) | 212