## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 11 | 5 | 51 | 35 | 129.5 | 6.55 | 50 | 75.5 | 42.5 | 0 | 43.4 | 5.7 | 222.5 | 5.7 | NO
| NG | 11 | 76 | 10 | 35 | 6.4 | 29.46 | 50 | 75.5 | 42.5 | 39.4 | 82.3 | 217.8 | 183.3 | 183.3 | NO
1 | OK | 5 | 3 | 51 | 35 | 129.5 | 4.45 | 50 | 75.5 | 42.5 | 40 | 43.4 | 217.9 | 222.5 | 217.9 | YES
| NG | 76 | 58 | 10 | 35 | 6.4 | 24.53 | 50 | 75.5 | 42.5 | 45 | 74.7 | 217.8 | 190.5 | 190.5 | NO
| NG | 76 | 78 | 38 | 35 | 106.5 | 4.93 | 50 | 75.5 | 42.5 | 32.3 | 48.3 | 7.9 | 220.1 | 7.9 | NO
2 | OK | 3 | 4 | 51 | 35 | 129.5 | 3.42 | 50 | 75.5 | 42.5 | 41.1 | 43.1 | 217.9 | 222.5 | 217.9 | YES
| NG | 58 | 57 | 10 | 35 | 6.4 | 23 | 50 | 75.5 | 42.5 | 45 | 72.5 | 217.8 | 192.5 | 192.5 | NO
| NG | 78 | 74 | 38 | 35 | 106.5 | 4.93 | 50 | 75.5 | 42.5 | 59.1 | 48.3 | 7.9 | 220.1 | 7.9 | NO
3 | ** OPTIMAL ** | 4 | 0 | 51 | 35 | 129.5 | 2.06 | 50 | 75.5 | 42.5 | 42.7 | 43.1 | 217.9 | 222.5 | 217.9 | YES
| NG | 57 | 59 | 10 | 35 | 6.4 | 21.81 | 50 | 75.5 | 42.5 | 45 | 70.9 | 217.8 | 194 | 194 | NO
| NG | 74 | 75 | 38 | 35 | 106.5 | 4.76 | 50 | 75.5 | 42.5 | 0 | 42.9 | 13.6 | 222.5 | 13.6 | NO
| NG | 0 | 1 | 2 | 35 | 131.1 | 1.45 | 50 | 75.5 | 42.5 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 42.5% (degenerate)
| NG | 0 | 54 | 51 | 35 | 129.5 | 0.61 | 50 | 75.5 | 42.5 | 0 | 43.1 | 5.4 | 222.5 | 5.4 | NO
| NG | 59 | 10 | 10 | 35 | 6.4 | 20.39 | 50 | 75.5 | 42.5 | 45 | 68.9 | 217.8 | 195.7 | 195.7 | NO
| NG | 75 | 77 | 77 | 35 | 142.9 | 4.76 | 50 | 75.5 | 42.5 | 70.1 | 42.9 | 201.7 | 222.5 | 201.7 | NO
| NG | 54 | 53 | 51 | 35 | 129.5 | 0.6 | 50 | 75.5 | 42.5 | 0 | 43.1 | 8.9 | 222.5 | 8.9 | NO
4 | OK | 10 | 12 | 12 | 35 | 58.6 | 20.39 | 50 | 75.5 | 42.5 | 45 | 42.5 | 217.8 | 222.5 | 217.8 | YES
5 | OK | 53 | 52 | 51 | 35 | 129.5 | 0.6 | 50 | 75.5 | 42.5 | 0 | 43.1 | 217.8 | 222.5 | 217.8 | YES
| NG | 12 | 8 | 8 | 13 | 69.3 | 20.39 | 50 | 75.5 | 42.5 | 49.9 | 69.5 | 217.5 | 192.3 | 192.3 | NO
| NG | 52 | 50 | 51 | 35 | 129.5 | 0.6 | 50 | 75.5 | 42.5 | 74.8 | 43.1 | 201.9 | 222.5 | 201.9 | NO
| NG | 8 | 9 | 9 | 13 | 98.9 | 10.92 | 50 | 75.5 | 42.5 | 61.1 | 56 | 215.6 | 208.9 | 208.9 | NO
6 | OK | 9 | 70 | 70 | 13 | 130.2 | 7.4 | 50 | 75.5 | 42.5 | 65.5 | 51.4 | 214 | 214.7 | 214 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 55-012847
TR_B (available) | 45-001324
TR_A Rated kVA | 100
TR_B Rated kVA | 100
TR_A Baseline Loading% | 75.5
TR_B Baseline Loading% | 42.5
Total Scenarios Evaluated | 22
Feasible Scenarios | 6
--- Optimal Solution ---
Switch Parent Node | 4
Switch Child Node | 0
Tie Node (TR_A side) | 51
Tie Node (TR_B side) | 35
Tie Line Distance (m) | 129.5
Load Transferred (kW) | 2.06
TR_A Loading After (%) | 42.7
TR_B Loading After (%) | 43.1
Minimum Voltage (V) | 217.9