## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 5 | 59 | 42 | 2 | 26.6 | 27.79 | 50 | 78.4 | 24.3 | [5 empty] | NO | TR_B sim: not converged
| NG | 59 | 58 | 42 | 2 | 26.6 | 27.79 | 50 | 78.4 | 24.3 | [5 empty] | NO | TR_B sim: not converged
| NG | 58 | 55 | 42 | 2 | 26.6 | 27.79 | 50 | 78.4 | 24.3 | [5 empty] | NO | TR_B sim: not converged
| NG | 55 | 32 | 42 | 2 | 26.6 | 24.21 | 50 | 78.4 | 24.3 | 0 | 86.9 | 6.2 | 147.4 | 6.2 | NO
| NG | 32 | 33 | 42 | 2 | 26.6 | 23.34 | 50 | 78.4 | 24.3 | 50.2 | 85.8 | 223.7 | 148.8 | 148.8 | NO
| NG | 33 | 37 | 42 | 2 | 26.6 | 21.44 | 50 | 78.4 | 24.3 | 51.2 | 80.8 | 223.5 | 155.2 | 155.2 | NO
| NG | 37 | 38 | 15 | 13 | 60.8 | 11.84 | 50 | 78.4 | 24.3 | 63.6 | 54.1 | 217.6 | 200.6 | 200.6 | NO
1 | OK | 37 | 36 | 48 | 1 | 35.4 | 4.18 | 50 | 78.4 | 24.3 | 72.2 | 33 | 211.5 | 212.4 | 211.5 | YES
| NG | 37 | 57 | 42 | 2 | 26.6 | 5.42 | 50 | 78.4 | 24.3 | 71.5 | 38 | 213.2 | 208.9 | 208.9 | NO
| NG | 38 | 43 | 15 | 13 | 60.8 | 10.79 | 50 | 78.4 | 24.3 | 65 | 51.6 | 217.6 | 200.9 | 200.9 | NO
2 | OK | 36 | 14 | 48 | 1 | 35.4 | 3.48 | 50 | 78.4 | 24.3 | 73.9 | 33 | 211.5 | 212.4 | 211.5 | YES
| NG | 57 | 39 | 42 | 2 | 26.6 | 5.42 | 50 | 78.4 | 24.3 | 71.5 | 38 | 213.2 | 208.9 | 208.9 | NO
| NG | 43 | 44 | 15 | 13 | 60.8 | 9.44 | 50 | 78.4 | 24.3 | 66.6 | 48.5 | 217.7 | 200.5 | 200.5 | NO
3 | OK | 14 | 12 | 48 | 1 | 35.4 | 3.46 | 50 | 78.4 | 24.3 | 74 | 30.2 | 211.5 | 216 | 211.5 | YES
4 | OK | 39 | 40 | 42 | 2 | 26.6 | 2.54 | 50 | 78.4 | 24.3 | 75.1 | 26.8 | 210.7 | 220.9 | 210.7 | YES
5 | OK | 44 | 16 | 15 | 13 | 60.8 | 1.46 | 50 | 78.4 | 24.3 | 76.5 | 27.8 | 210 | 220.6 | 210 | YES
6 | OK | 44 | 45 | 45 | 13 | 94.4 | 0.3 | 50 | 78.4 | 24.3 | 73.6 | 25 | 211.7 | 223.5 | 211.7 | YES
7 | ** OPTIMAL ** | 44 | 34 | 34 | 13 | 137.4 | 4.18 | 50 | 78.4 | 24.3 | 73 | 34.7 | 214.1 | 212.1 | 212.1 | YES
8 | OK | 12 | 13 | 48 | 1 | 35.4 | 2.42 | 50 | 78.4 | 24.3 | 75.3 | 30.2 | 210.6 | 216 | 210.6 | YES
| NG | 40 | 41 | 42 | 2 | 26.6 | 1.05 | 50 | 78.4 | 24.3 | 77 | 26.8 | 209.4 | 220.9 | 209.4 | NO
| NG | 16 | 15 | 15 | 13 | 60.8 | 0.5 | 50 | 78.4 | 24.3 | 77.7 | 24.3 | 209 | 223.4 | 209 | NO
| NG | 34 | 35 | 35 | 13 | 140.3 | 0.67 | 50 | 78.4 | 24.3 | 77.5 | 24.3 | 209.4 | 223.4 | 209.4 | NO
| NG | 13 | 47 | 48 | 1 | 35.4 | 1.06 | 50 | 78.4 | 24.3 | 77 | 26.8 | 209.4 | 220.2 | 209.4 | NO
| NG | 47 | 11 | 48 | 1 | 35.4 | 0.77 | 50 | 78.4 | 24.3 | 77.4 | 26.1 | 209.2 | 221 | 209.2 | NO
| NG | 11 | 10 | 10 | 1 | 144.3 | 0.73 | 50 | 78.4 | 24.3 | 77.4 | 26 | 209.2 | 221.2 | 209.2 | NO
| NG | 11 | 19 | 48 | 1 | 35.4 | 0.04 | 50 | 78.4 | 24.3 | 78.3 | 24.4 | 208.5 | 223.3 | 208.5 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 55-930097
TR_B (available) | 65-014011
TR_A Rated kVA | 100
TR_B Rated kVA | 50
TR_A Baseline Loading% | 78.4
TR_B Baseline Loading% | 24.3
Total Scenarios Evaluated | 26
Feasible Scenarios | 8
--- Optimal Solution ---
Switch Parent Node | 44
Switch Child Node | 34
Tie Node (TR_A side) | 34
Tie Node (TR_B side) | 13
Tie Line Distance (m) | 137.4
Load Transferred (kW) | 4.18
TR_A Loading After (%) | 73
TR_B Loading After (%) | 34.7
Minimum Voltage (V) | 212.1