## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 6 | 19 | 30 | 32 | 81.6 | 5.92 | 50 | 21.6 | 16.6 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 19 | 20 | 30 | 32 | 81.6 | 2.27 | 50 | 21.6 | 16.6 | 16.4 | 18.3 | 227 | 225.2 | 225.2 | YES
2 | OK | 20 | 24 | 30 | 32 | 81.6 | 1.65 | 50 | 21.6 | 16.6 | 17.8 | 17.8 | 227 | 226.7 | 226.7 | YES
3 | OK | 24 | 0 | 30 | 32 | 81.6 | 1.65 | 50 | 21.6 | 16.6 | 17.8 | 17.8 | 227 | 226.7 | 226.7 | YES
4 | OK | 0 | 1 | 30 | 32 | 81.6 | 1.33 | 50 | 21.6 | 16.6 | 18.5 | 17.6 | 226.8 | 226.9 | 226.8 | YES
5 | OK | 0 | 25 | 26 | 33 | 100 | 0.32 | 50 | 21.6 | 16.6 | 20.8 | 16.6 | 226.8 | 226.9 | 226.8 | YES
6 | ** OPTIMAL ** | 1 | 10 | 30 | 32 | 81.6 | 0.62 | 50 | 21.6 | 16.6 | 19.2 | 17.1 | 226.8 | 226.9 | 226.8 | YES
7 | OK | 10 | 8 | 30 | 32 | 81.6 | 0.62 | 50 | 21.6 | 16.6 | 20.2 | 17.1 | 226.6 | 226.9 | 226.6 | YES
8 | OK | 8 | 27 | 30 | 32 | 81.6 | 0.02 | 50 | 21.6 | 16.6 | 21.5 | 16.6 | 226.6 | 226.9 | 226.6 | YES
9 | OK | 27 | 28 | 30 | 32 | 81.6 | 0.02 | 50 | 21.6 | 16.6 | 21.5 | 16.6 | 226.6 | 226.9 | 226.6 | YES
10 | OK | 28 | 29 | 30 | 32 | 81.6 | 0.02 | 50 | 21.6 | 16.6 | 21.5 | 16.6 | 226.6 | 226.9 | 226.6 | YES
11 | OK | 29 | 30 | 30 | 32 | 81.6 | 0.02 | 50 | 21.6 | 16.6 | 21.5 | 16.6 | 226.6 | 226.9 | 226.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 55-940578
TR_B (available) | 63-005613
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 21.6
TR_B Baseline Loading% | 16.6
Total Scenarios Evaluated | 12
Feasible Scenarios | 11
--- Optimal Solution ---
Switch Parent Node | 1
Switch Child Node | 10
Tie Node (TR_A side) | 30
Tie Node (TR_B side) | 32
Tie Line Distance (m) | 81.6
Load Transferred (kW) | 0.62
TR_A Loading After (%) | 19.2
TR_B Loading After (%) | 17.1
Minimum Voltage (V) | 226.8