## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 11 | 78 | 19 | 8 | 198.9 | 27.2 | 50 | 81.1 | 33.5 | 60.7 | 46.1 | 209.3 | 181.4 | 181.4 | NO
| NG | 55 | 75 | 99 | 18 | 96.4 | 21.16 | 50 | 81.1 | 33.5 | 65.1 | 59.3 | 211.1 | 208.4 | 208.4 | NO
| NG | 78 | 61 | 19 | 8 | 198.9 | 27.1 | 50 | 81.1 | 33.5 | 60.7 | 45.9 | 209.3 | 182 | 182 | NO
| NG | 75 | 92 | 99 | 18 | 96.4 | 21.05 | 50 | 81.1 | 33.5 | 65.2 | 58.3 | 211.1 | 207.7 | 207.7 | NO
| NG | 61 | 60 | 19 | 8 | 198.9 | 26.08 | 50 | 81.1 | 33.5 | 61.5 | 45.9 | 209.3 | 182 | 182 | NO
| NG | 92 | 93 | 99 | 18 | 96.4 | 19.98 | 50 | 81.1 | 33.5 | 66 | 57.8 | 211.1 | 207.6 | 207.6 | NO
| NG | 60 | 34 | 19 | 8 | 198.9 | 22.45 | 50 | 81.1 | 33.5 | 64.1 | 42.2 | 209 | 194.2 | 194.2 | NO
1 | OK | 93 | 73 | 99 | 18 | 96.4 | 19.09 | 50 | 81.1 | 33.5 | 66.6 | 56.6 | 210.8 | 210.4 | 210.4 | YES
| NG | 34 | 35 | 19 | 8 | 198.9 | 16.8 | 50 | 81.1 | 33.5 | 68.3 | 41.4 | 208.9 | 196.8 | 196.8 | NO
| NG | 73 | 74 | 99 | 18 | 96.4 | 18.56 | 50 | 81.1 | 33.5 | 67 | 56 | 210.9 | 210 | 210 | NO
| NG | 35 | 25 | 19 | 8 | 198.9 | 4.3 | 50 | 81.1 | 33.5 | 77.8 | 34.4 | 208.2 | 221.6 | 208.2 | NO
2 | OK | 74 | 90 | 99 | 18 | 96.4 | 15.61 | 50 | 81.1 | 33.5 | 69.2 | 52.2 | 210.6 | 211.7 | 210.6 | YES
| NG | 25 | 24 | 19 | 8 | 198.9 | 4.08 | 50 | 81.1 | 33.5 | 78 | 34.4 | 208.2 | 221.6 | 208.2 | NO
3 | OK | 90 | 91 | 99 | 18 | 96.4 | 15.6 | 50 | 81.1 | 33.5 | 69.2 | 52.2 | 210.6 | 211.7 | 210.6 | YES
4 | OK | 91 | 121 | 99 | 18 | 96.4 | 15.14 | 50 | 81.1 | 33.5 | 69.5 | 51.6 | 210.6 | 211.6 | 210.6 | YES
5 | ** OPTIMAL ** | 121 | 68 | 99 | 18 | 96.4 | 14.45 | 50 | 81.1 | 33.5 | 70.1 | 50.8 | 210.7 | 211.4 | 210.7 | YES
6 | OK | 68 | 70 | 99 | 18 | 96.4 | 13.06 | 50 | 81.1 | 33.5 | 71.1 | 49 | 210.4 | 213.8 | 210.4 | YES
| NG | 70 | 67 | 99 | 18 | 96.4 | 10.81 | 50 | 81.1 | 33.5 | 72.8 | 46.2 | 209.5 | 219.9 | 209.5 | NO
| NG | 67 | 66 | 99 | 18 | 96.4 | 8.8 | 50 | 81.1 | 33.5 | 74.3 | 43.8 | 209.4 | 219.8 | 209.4 | NO
| NG | 66 | 18 | 99 | 18 | 96.4 | 8.45 | 50 | 81.1 | 33.5 | 74.6 | 43.4 | 209.5 | 219.6 | 209.5 | NO
| NG | 18 | 17 | 99 | 18 | 96.4 | 8.45 | 50 | 81.1 | 33.5 | 74.6 | 43.4 | 209.5 | 219.6 | 209.5 | NO
| NG | 17 | 16 | 99 | 18 | 96.4 | 5.43 | 50 | 81.1 | 33.5 | 76.9 | 39.8 | 208.7 | 221.5 | 208.7 | NO
| NG | 16 | 15 | 99 | 18 | 96.4 | 1.94 | 50 | 81.1 | 33.5 | 79.6 | 35.7 | 208.7 | 221.6 | 208.7 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 56-002659
TR_B (available) | 58-000581
TR_A Rated kVA | 160
TR_B Rated kVA | 100
TR_A Baseline Loading% | 81.1
TR_B Baseline Loading% | 33.5
Total Scenarios Evaluated | 23
Feasible Scenarios | 6
--- Optimal Solution ---
Switch Parent Node | 121
Switch Child Node | 68
Tie Node (TR_A side) | 99
Tie Node (TR_B side) | 18
Tie Line Distance (m) | 96.4
Load Transferred (kW) | 14.45
TR_A Loading After (%) | 70.1
TR_B Loading After (%) | 50.8
Minimum Voltage (V) | 210.7