## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 74 | 90 | 13 | 14 | 56.3 | 15.61 | 50 | 81.1 | 44.9 | 69.2 | 59.6 | 210.6 | 213 | 210.6 | YES
2 | OK | 90 | 91 | 13 | 14 | 56.3 | 15.6 | 50 | 81.1 | 44.9 | 69.2 | 59.6 | 210.6 | 213 | 210.6 | YES
3 | OK | 91 | 121 | 13 | 14 | 56.3 | 15.14 | 50 | 81.1 | 44.9 | 69.5 | 59.6 | 210.6 | 213 | 210.6 | YES
4 | ** OPTIMAL ** | 121 | 68 | 13 | 14 | 56.3 | 14.45 | 50 | 81.1 | 44.9 | 70.1 | 59.6 | 210.7 | 213 | 210.7 | YES
5 | OK | 68 | 70 | 13 | 14 | 56.3 | 13.06 | 50 | 81.1 | 44.9 | 71.1 | 57.9 | 210.4 | 215 | 210.4 | YES
| NG | 70 | 67 | 13 | 14 | 56.3 | 10.81 | 50 | 81.1 | 44.9 | 72.8 | 53.1 | 209.5 | 220.1 | 209.5 | NO
| NG | 67 | 66 | 13 | 14 | 56.3 | 8.8 | 50 | 81.1 | 44.9 | 74.3 | 52.6 | 209.4 | 220.6 | 209.4 | NO
| NG | 66 | 18 | 13 | 14 | 56.3 | 8.45 | 50 | 81.1 | 44.9 | 74.6 | 52.6 | 209.5 | 220.6 | 209.5 | NO
| NG | 18 | 17 | 13 | 14 | 56.3 | 8.45 | 50 | 81.1 | 44.9 | 74.6 | 52.6 | 209.5 | 220.6 | 209.5 | NO
| NG | 17 | 16 | 13 | 14 | 56.3 | 5.43 | 50 | 81.1 | 44.9 | 76.9 | 48.8 | 208.7 | 223.2 | 208.7 | NO
| NG | 16 | 15 | 13 | 14 | 56.3 | 1.94 | 50 | 81.1 | 44.9 | 79.6 | 47.7 | 208.7 | 223.1 | 208.7 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 56-002659
TR_B (available) | 60-012535
TR_A Rated kVA | 160
TR_B Rated kVA | 50
TR_A Baseline Loading% | 81.1
TR_B Baseline Loading% | 44.9
Total Scenarios Evaluated | 11
Feasible Scenarios | 5
--- Optimal Solution ---
Switch Parent Node | 121
Switch Child Node | 68
Tie Node (TR_A side) | 13
Tie Node (TR_B side) | 14
Tie Line Distance (m) | 56.3
Load Transferred (kW) | 14.45
TR_A Loading After (%) | 70.1
TR_B Loading After (%) | 59.6
Minimum Voltage (V) | 210.7