## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 51 | 52 | 82 | 7 | 6.7 | 55.91 | 50 | 81.1 | 19.2 | [5 empty] | NO | TR_B sim: not converged
| NG | 52 | 53 | 82 | 7 | 6.7 | 55.14 | 50 | 81.1 | 19.2 | [5 empty] | NO | TR_B sim: not converged
| NG | 53 | 54 | 82 | 7 | 6.7 | 53.98 | 50 | 81.1 | 19.2 | [5 empty] | NO | TR_B sim: not converged
| NG | 54 | 55 | 82 | 7 | 6.7 | 53.82 | 50 | 81.1 | 19.2 | [5 empty] | NO | TR_B sim: not converged
1 | ** OPTIMAL ** | 55 | 76 | 82 | 7 | 6.7 | 10.39 | 50 | 81.1 | 19.2 | 73.3 | 27.9 | 210.2 | 218.9 | 210.2 | YES
| NG | 76 | 77 | 82 | 7 | 6.7 | 9.27 | 50 | 81.1 | 19.2 | 74.2 | 26.9 | 209.9 | 220.7 | 209.9 | NO
| NG | 77 | 101 | 82 | 7 | 6.7 | 7.85 | 50 | 81.1 | 19.2 | 74.6 | 25.2 | 209.7 | 222.2 | 209.7 | NO
| NG | 101 | 110 | 82 | 7 | 6.7 | 6.66 | 50 | 81.1 | 19.2 | 76.1 | 24.3 | 209.7 | 222.2 | 209.7 | NO
| NG | 110 | 111 | 82 | 7 | 6.7 | 6.09 | 50 | 81.1 | 19.2 | 76.5 | 23.6 | 209.4 | 223.3 | 209.4 | NO
| NG | 111 | 127 | 82 | 7 | 6.7 | 5.66 | 50 | 81.1 | 19.2 | 76.9 | 23.1 | 209.4 | 223.2 | 209.4 | NO
| NG | 127 | 79 | 82 | 7 | 6.7 | 5.04 | 50 | 81.1 | 19.2 | 77.3 | 22.4 | 209.1 | 224.4 | 209.1 | NO
| NG | 79 | 80 | 82 | 7 | 6.7 | 3.04 | 50 | 81.1 | 19.2 | 78.8 | 20.6 | 208.4 | 225 | 208.4 | NO
| NG | 79 | 125 | 128 | 8 | 117.6 | 2 | 50 | 81.1 | 19.2 | 79.6 | 20.9 | 208.8 | 225.2 | 208.8 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 56-002659
TR_B (available) | 66-018354
TR_A Rated kVA | 160
TR_B Rated kVA | 100
TR_A Baseline Loading% | 81.1
TR_B Baseline Loading% | 19.2
Total Scenarios Evaluated | 13
Feasible Scenarios | 1
--- Optimal Solution ---
Switch Parent Node | 55
Switch Child Node | 76
Tie Node (TR_A side) | 82
Tie Node (TR_B side) | 7
Tie Line Distance (m) | 6.7
Load Transferred (kW) | 10.39
TR_A Loading After (%) | 73.3
TR_B Loading After (%) | 27.9
Minimum Voltage (V) | 210.2