## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 23 | 11 | 97 | 49 | 46.1 | 50.05 | 50 | 81.1 | 48.7 | [5 empty] | NO | TR_B sim: not converged
| NG | 11 | 12 | 100 | 44 | 114.8 | 21.88 | 50 | 81.1 | 48.7 | [5 empty] | NO | TR_B sim: not converged
| NG | 11 | 78 | 97 | 49 | 46.1 | 27.2 | 50 | 81.1 | 48.7 | [5 empty] | NO | TR_B sim: not converged
| NG | 55 | 75 | 13 | 76 | 177.5 | 21.16 | 50 | 81.1 | 48.7 | 65.1 | 61.2 | 211.1 | 200.3 | 200.3 | NO
| NG | 12 | 2 | 100 | 44 | 114.8 | 21.06 | 50 | 81.1 | 48.7 | [5 empty] | NO | TR_B sim: not converged
| NG | 78 | 61 | 97 | 49 | 46.1 | 27.1 | 50 | 81.1 | 48.7 | [5 empty] | NO | TR_B sim: not converged
| NG | 75 | 92 | 13 | 76 | 177.5 | 21.05 | 50 | 81.1 | 48.7 | 65.2 | 61.1 | 211.1 | 200.9 | 200.9 | NO
| NG | 2 | 3 | 104 | 52 | 115 | 17.51 | 50 | 81.1 | 48.7 | 67.9 | 51.9 | 208.6 | 206 | 206 | NO
| NG | 2 | 4 | 100 | 44 | 114.8 | 3.54 | 50 | 81.1 | 48.7 | 78.4 | 51.6 | 208.1 | 208.1 | 208.1 | NO
| NG | 61 | 60 | 97 | 49 | 46.1 | 26.08 | 50 | 81.1 | 48.7 | [5 empty] | NO | TR_B sim: not converged
| NG | 92 | 93 | 13 | 76 | 177.5 | 19.98 | 50 | 81.1 | 48.7 | 66 | 60.8 | 211.1 | 202 | 202 | NO
| NG | 3 | 37 | 104 | 52 | 115 | 17.51 | 50 | 81.1 | 48.7 | 67.9 | 51.9 | 208.6 | 206 | 206 | NO
| NG | 4 | 5 | 100 | 44 | 114.8 | 2.68 | 50 | 81.1 | 48.7 | 79.1 | 50.8 | 208.1 | 211.1 | 208.1 | NO
| NG | 60 | 34 | 97 | 49 | 46.1 | 22.45 | 50 | 81.1 | 48.7 | [5 empty] | NO | TR_B sim: not converged
| NG | 93 | 73 | 13 | 76 | 177.5 | 19.09 | 50 | 81.1 | 48.7 | 66.6 | 60.2 | 210.8 | 202.2 | 202.2 | NO
| NG | 37 | 38 | 104 | 52 | 115 | 17.39 | 50 | 81.1 | 48.7 | 68 | 51.9 | 208.6 | 206 | 206 | NO
| NG | 5 | 1 | 100 | 44 | 114.8 | 2.05 | 50 | 81.1 | 48.7 | 79.6 | 50.3 | 208.1 | 213.2 | 208.1 | NO
| NG | 34 | 35 | 97 | 49 | 46.1 | 16.8 | 50 | 81.1 | 48.7 | 68.3 | 67.7 | 208.9 | 148.1 | 148.1 | NO
| NG | 73 | 74 | 13 | 76 | 177.5 | 18.56 | 50 | 81.1 | 48.7 | 67 | 60.2 | 210.9 | 202.2 | 202.2 | NO
| NG | 38 | 6 | 104 | 52 | 115 | 16.89 | 50 | 81.1 | 48.7 | 68.4 | 51.9 | 208.6 | 206 | 206 | NO
| NG | 35 | 59 | 97 | 49 | 46.1 | 12.5 | 50 | 81.1 | 48.7 | 71.5 | 60.9 | 208.8 | 174.5 | 174.5 | NO
| NG | 35 | 25 | 26 | 0 | 122.5 | 4.3 | 50 | 81.1 | 48.7 | 77.8 | 49.5 | 208.2 | 212.8 | 208.2 | NO
| NG | 74 | 90 | 13 | 76 | 177.5 | 15.61 | 50 | 81.1 | 48.7 | 69.2 | 58.2 | 210.6 | 208.2 | 208.2 | NO
| NG | 6 | 8 | 104 | 52 | 115 | 6.34 | 50 | 81.1 | 48.7 | 76.3 | 50.1 | 208.3 | 214.4 | 208.3 | NO
| NG | 59 | 87 | 97 | 49 | 46.1 | 11.03 | 50 | 81.1 | 48.7 | 72.7 | 59.1 | 208.8 | 180.8 | 180.8 | NO
| NG | 25 | 24 | 26 | 0 | 122.5 | 4.08 | 50 | 81.1 | 48.7 | 78 | 49.3 | 208.2 | 213.6 | 208.2 | NO
| NG | 90 | 91 | 13 | 76 | 177.5 | 15.6 | 50 | 81.1 | 48.7 | 69.2 | 58.2 | 210.6 | 208.2 | 208.2 | NO
| NG | 8 | 113 | 104 | 52 | 115 | 5.79 | 50 | 81.1 | 48.7 | 76.7 | 49.7 | 208.3 | 215.8 | 208.3 | NO
| NG | 87 | 36 | 97 | 49 | 46.1 | 11.03 | 50 | 81.1 | 48.7 | 72.7 | 59.1 | 208.8 | 180.8 | 180.8 | NO
| NG | 91 | 121 | 13 | 76 | 177.5 | 15.14 | 50 | 81.1 | 48.7 | 69.5 | 57.8 | 210.6 | 208 | 208 | NO
| NG | 113 | 129 | 104 | 52 | 115 | 4.83 | 50 | 81.1 | 48.7 | 77.4 | 49.7 | 208.3 | 215.8 | 208.3 | NO
| NG | 36 | 30 | 97 | 49 | 46.1 | 9.66 | 50 | 81.1 | 48.7 | 73.7 | 57.5 | 208.9 | 186.2 | 186.2 | NO
| NG | 121 | 68 | 13 | 76 | 177.5 | 14.45 | 50 | 81.1 | 48.7 | 70.1 | 57.3 | 210.7 | 207.7 | 207.7 | NO
| NG | 129 | 120 | 104 | 52 | 115 | 4.82 | 50 | 81.1 | 48.7 | 77.4 | 49.7 | 208.3 | 215.8 | 208.3 | NO
| NG | 30 | 31 | 31 | 49 | 154.2 | 3.74 | 50 | 81.1 | 48.7 | 78.3 | 51.8 | 208.7 | 204.6 | 204.6 | NO
| NG | 30 | 130 | 97 | 49 | 46.1 | 5.92 | 50 | 81.1 | 48.7 | 76.5 | 53.8 | 208.3 | 199.6 | 199.6 | NO
1 | ** OPTIMAL ** | 68 | 70 | 13 | 76 | 177.5 | 13.06 | 50 | 81.1 | 48.7 | 71.1 | 56.2 | 210.4 | 210.5 | 210.4 | YES
| NG | 120 | 102 | 104 | 52 | 115 | 2.11 | 50 | 81.1 | 48.7 | 79.5 | 49.7 | 208.3 | 215.8 | 208.3 | NO
| NG | 31 | 86 | 86 | 49 | 155 | 2.68 | 50 | 81.1 | 48.7 | 79.1 | 48.7 | 208.5 | 215.4 | 208.5 | NO
| NG | 130 | 32 | 97 | 49 | 46.1 | 5.92 | 50 | 81.1 | 48.7 | 76.5 | 53.8 | 208.3 | 199.6 | 199.6 | NO
| NG | 70 | 67 | 13 | 76 | 177.5 | 10.81 | 50 | 81.1 | 48.7 | 72.8 | 54.4 | 209.5 | 214.4 | 209.5 | NO
| NG | 32 | 33 | 33 | 49 | 103.2 | 2.02 | 50 | 81.1 | 48.7 | 79.6 | 50.3 | 208.1 | 210.1 | 208.1 | NO
| NG | 32 | 94 | 97 | 49 | 46.1 | 3.9 | 50 | 81.1 | 48.7 | 78.1 | 51.9 | 208.3 | 205.6 | 205.6 | NO
| NG | 67 | 66 | 13 | 76 | 177.5 | 8.8 | 50 | 81.1 | 48.7 | 74.3 | 53.7 | 209.4 | 214.9 | 209.4 | NO
| NG | 66 | 18 | 13 | 76 | 177.5 | 8.45 | 50 | 81.1 | 48.7 | 74.6 | 53.7 | 209.5 | 214.9 | 209.5 | NO
| NG | 18 | 17 | 13 | 76 | 177.5 | 8.45 | 50 | 81.1 | 48.7 | 74.6 | 53.7 | 209.5 | 214.9 | 209.5 | NO
| NG | 17 | 16 | 13 | 76 | 177.5 | 5.43 | 50 | 81.1 | 48.7 | 76.9 | 51.3 | 208.7 | 215.1 | 208.7 | NO
| NG | 16 | 15 | 13 | 76 | 177.5 | 1.94 | 50 | 81.1 | 48.7 | 79.6 | 49.8 | 208.7 | 215.3 | 208.7 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 56-002659
TR_B (available) | 67-030316
TR_A Rated kVA | 160
TR_B Rated kVA | 160
TR_A Baseline Loading% | 81.1
TR_B Baseline Loading% | 48.7
Total Scenarios Evaluated | 48
Feasible Scenarios | 1
--- Optimal Solution ---
Switch Parent Node | 68
Switch Child Node | 70
Tie Node (TR_A side) | 13
Tie Node (TR_B side) | 76
Tie Line Distance (m) | 177.5
Load Transferred (kW) | 13.06
TR_A Loading After (%) | 71.1
TR_B Loading After (%) | 56.2
Minimum Voltage (V) | 210.4