## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 17 | 18 | 0 | 11 | 0.7 | 7.99 | 50 | 86.8 | 39.5 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 18 | 27 | 0 | 11 | 0.7 | 7.99 | 50 | 86.8 | 39.5 | 55.8 | 72.4 | 218.1 | 203.8 | 203.8 | NO
| NG | 27 | 43 | 0 | 11 | 0.7 | 7.45 | 50 | 86.8 | 39.5 | 57.8 | 70 | 217.9 | 205.8 | 205.8 | NO
| NG | 43 | 26 | 0 | 11 | 0.7 | 7.45 | 50 | 86.8 | 39.5 | 57.8 | 70 | 217.9 | 205.8 | 205.8 | NO
| NG | 26 | 25 | 0 | 11 | 0.7 | 7.17 | 50 | 86.8 | 39.5 | 58.9 | 68.8 | 217.7 | 205.6 | 205.6 | NO
| NG | 25 | 24 | 0 | 11 | 0.7 | 6.77 | 50 | 86.8 | 39.5 | 60.4 | 67.1 | 217.6 | 207 | 207 | NO
| NG | 24 | 23 | 0 | 11 | 0.7 | 5.77 | 50 | 86.8 | 39.5 | 64.3 | 62.9 | 217 | 207.8 | 207.8 | NO
1 | OK | 23 | 22 | 0 | 11 | 0.7 | 4.87 | 50 | 86.8 | 39.5 | 67.7 | 59 | 217 | 212.8 | 212.8 | YES
2 | OK | 22 | 21 | 0 | 11 | 0.7 | 4.38 | 50 | 86.8 | 39.5 | 69.6 | 57 | 217 | 215.4 | 215.4 | YES
3 | ** OPTIMAL ** | 21 | 20 | 0 | 11 | 0.7 | 3.93 | 50 | 86.8 | 39.5 | 71.4 | 55.1 | 216.9 | 217.6 | 216.9 | YES
4 | OK | 20 | 19 | 0 | 11 | 0.7 | 2.1 | 50 | 86.8 | 39.5 | 78.5 | 47.8 | 216.1 | 220.3 | 216.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 56-003004
TR_B (available) | 53-009945
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 86.8
TR_B Baseline Loading% | 39.5
Total Scenarios Evaluated | 11
Feasible Scenarios | 4
--- Optimal Solution ---
Switch Parent Node | 21
Switch Child Node | 20
Tie Node (TR_A side) | 0
Tie Node (TR_B side) | 11
Tie Line Distance (m) | 0.7
Load Transferred (kW) | 3.93
TR_A Loading After (%) | 71.4
TR_B Loading After (%) | 55.1
Minimum Voltage (V) | 216.9