## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 17 | 29 | 11 | 5 | 31 | 14.25 | 50 | 86.8 | 9.6 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 29 | 30 | 11 | 5 | 31 | 12.44 | 50 | 86.8 | 9.6 | 37.9 | 33.1 | 219.7 | 203.9 | 203.9 | NO
| NG | 30 | 31 | 11 | 5 | 31 | 11.59 | 50 | 86.8 | 9.6 | 41.2 | 29.2 | 219.1 | 208.3 | 208.3 | NO
1 | OK | 31 | 28 | 11 | 5 | 31 | 10.83 | 50 | 86.8 | 9.6 | 44.1 | 25.8 | 218.5 | 212 | 212 | YES
2 | OK | 28 | 4 | 11 | 5 | 31 | 9.92 | 50 | 86.8 | 9.6 | 47.7 | 21.9 | 217.8 | 216 | 216 | YES
3 | OK | 4 | 3 | 11 | 5 | 31 | 8.38 | 50 | 86.8 | 9.6 | 53.6 | 21.9 | 217.8 | 216 | 216 | YES
4 | ** OPTIMAL ** | 3 | 5 | 11 | 5 | 31 | 4.61 | 50 | 86.8 | 9.6 | 68.3 | 17.1 | 216.9 | 221.1 | 216.9 | YES
5 | OK | 3 | 32 | 47 | 5 | 114.4 | 3.77 | 50 | 86.8 | 9.6 | 71.7 | 24.9 | 216.3 | 213.4 | 213.4 | YES
6 | OK | 5 | 6 | 11 | 5 | 31 | 3.35 | 50 | 86.8 | 9.6 | 73.3 | 14.6 | 216.4 | 223.3 | 216.4 | YES
7 | OK | 32 | 39 | 47 | 5 | 114.4 | 3.05 | 50 | 86.8 | 9.6 | 74.6 | 21.9 | 215.7 | 216.3 | 215.7 | YES
8 | OK | 6 | 7 | 11 | 5 | 31 | 2.3 | 50 | 86.8 | 9.6 | 77.6 | 14.6 | 216.4 | 223.3 | 216.4 | YES
9 | OK | 39 | 38 | 47 | 5 | 114.4 | 3.05 | 50 | 86.8 | 9.6 | 74.6 | 21.9 | 215.7 | 216.3 | 215.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 56-003004
TR_B (available) | 64-020554
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 86.8
TR_B Baseline Loading% | 9.6
Total Scenarios Evaluated | 12
Feasible Scenarios | 9
--- Optimal Solution ---
Switch Parent Node | 3
Switch Child Node | 5
Tie Node (TR_A side) | 11
Tie Node (TR_B side) | 5
Tie Line Distance (m) | 31
Load Transferred (kW) | 4.61
TR_A Loading After (%) | 68.3
TR_B Loading After (%) | 17.1
Minimum Voltage (V) | 216.9