## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 17 | 18 | 23 | 26 | 36.4 | 7.99 | 50 | 86.8 | 35.6 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 17 | 29 | 39 | 12 | 37.5 | 14.25 | 50 | 86.8 | 35.6 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 18 | 27 | 23 | 26 | 36.4 | 7.99 | 50 | 86.8 | 35.6 | 55.8 | 45 | 218.1 | 211.9 | 211.9 | YES
| NG | 29 | 30 | 39 | 12 | 37.5 | 12.44 | 50 | 86.8 | 35.6 | 37.9 | 51.3 | 219.7 | 205.1 | 205.1 | NO
2 | OK | 27 | 43 | 23 | 26 | 36.4 | 7.45 | 50 | 86.8 | 35.6 | 57.8 | 44.4 | 217.9 | 212 | 212 | YES
| NG | 30 | 31 | 39 | 12 | 37.5 | 11.59 | 50 | 86.8 | 35.6 | 41.2 | 50.3 | 219.1 | 204.8 | 204.8 | NO
3 | OK | 43 | 26 | 23 | 26 | 36.4 | 7.45 | 50 | 86.8 | 35.6 | 57.8 | 44.4 | 217.9 | 212 | 212 | YES
| NG | 31 | 28 | 39 | 12 | 37.5 | 10.83 | 50 | 86.8 | 35.6 | 44.1 | 49.4 | 218.5 | 204.5 | 204.5 | NO
4 | OK | 26 | 25 | 23 | 26 | 36.4 | 7.17 | 50 | 86.8 | 35.6 | 58.9 | 44 | 217.7 | 212.1 | 212.1 | YES
| NG | 28 | 4 | 39 | 12 | 37.5 | 9.92 | 50 | 86.8 | 35.6 | 47.7 | 48.3 | 217.8 | 204.1 | 204.1 | NO
5 | OK | 25 | 24 | 23 | 26 | 36.4 | 6.77 | 50 | 86.8 | 35.6 | 60.4 | 43.6 | 217.6 | 212.1 | 212.1 | YES
| NG | 4 | 3 | 39 | 12 | 37.5 | 8.38 | 50 | 86.8 | 35.6 | 53.6 | 46.2 | 217.8 | 206.4 | 206.4 | NO
6 | OK | 24 | 23 | 23 | 26 | 36.4 | 5.77 | 50 | 86.8 | 35.6 | 64.3 | 42.4 | 217 | 212.3 | 212.3 | YES
7 | ** OPTIMAL ** | 3 | 5 | 13 | 17 | 82.2 | 4.61 | 50 | 86.8 | 35.6 | 68.3 | 37.9 | 216.9 | 213.6 | 213.6 | YES
| NG | 3 | 32 | 39 | 12 | 37.5 | 3.77 | 50 | 86.8 | 35.6 | 71.7 | 40.3 | 216.3 | 209.7 | 209.7 | NO
8 | OK | 23 | 22 | 22 | 26 | 49.1 | 4.87 | 50 | 86.8 | 35.6 | 67.7 | 41.3 | 217 | 212.3 | 212.3 | YES
9 | OK | 5 | 6 | 13 | 17 | 82.2 | 3.35 | 50 | 86.8 | 35.6 | 73.3 | 37.1 | 216.4 | 213.4 | 213.4 | YES
| NG | 32 | 39 | 39 | 12 | 37.5 | 3.05 | 50 | 86.8 | 35.6 | 74.6 | 39.5 | 215.7 | 209.4 | 209.4 | NO
10 | OK | 22 | 21 | 21 | 26 | 84.2 | 4.38 | 50 | 86.8 | 35.6 | 69.6 | 40.7 | 217 | 212.3 | 212.3 | YES
11 | OK | 6 | 7 | 13 | 17 | 82.2 | 2.3 | 50 | 86.8 | 35.6 | 77.6 | 37.1 | 216.4 | 213.4 | 213.4 | YES
| NG | 39 | 38 | 48 | 30 | 38 | 3.05 | 50 | 86.8 | 35.6 | 74.6 | 39.5 | 215.7 | 209.3 | 209.3 | NO
12 | OK | 21 | 20 | 20 | 26 | 110.5 | 3.93 | 50 | 86.8 | 35.6 | 71.4 | 40.2 | 216.9 | 212.3 | 212.3 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 56-003004
TR_B (available) | 67-033377
TR_A Rated kVA | 30
TR_B Rated kVA | 100
TR_A Baseline Loading% | 86.8
TR_B Baseline Loading% | 35.6
Total Scenarios Evaluated | 22
Feasible Scenarios | 12
--- Optimal Solution ---
Switch Parent Node | 3
Switch Child Node | 5
Tie Node (TR_A side) | 13
Tie Node (TR_B side) | 17
Tie Line Distance (m) | 82.2
Load Transferred (kW) | 4.61
TR_A Loading After (%) | 68.3
TR_B Loading After (%) | 37.9
Minimum Voltage (V) | 213.6