## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 29 | 28 | 33 | 9 | 130.5 | 10.5 | 50 | 85.8 | 50.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 28 | 34 | 33 | 9 | 130.5 | 10.5 | 50 | 85.8 | 50.8 | 45 | 68.1 | 222.2 | 192.9 | 192.9 | NO
| NG | 34 | 5 | 33 | 9 | 130.5 | 9.14 | 50 | 85.8 | 50.8 | 50.2 | 63.9 | 221.2 | 201.9 | 201.9 | NO
| NG | 5 | 4 | 33 | 9 | 130.5 | 9.14 | 50 | 85.8 | 50.8 | 50.2 | 63.9 | 221.2 | 201.9 | 201.9 | NO
| NG | 4 | 6 | 33 | 9 | 130.5 | 7.28 | 50 | 85.8 | 50.8 | 57.3 | 63.4 | 221 | 202.8 | 202.8 | NO
| NG | 6 | 8 | 33 | 9 | 130.5 | 6.91 | 50 | 85.8 | 50.8 | 57.3 | 63.4 | 221 | 202.8 | 202.8 | NO
| NG | 8 | 7 | 33 | 9 | 130.5 | 6.91 | 50 | 85.8 | 50.8 | 58.7 | 63.4 | 221 | 202.8 | 202.8 | NO
1 | OK | 7 | 9 | 33 | 9 | 130.5 | 5.24 | 50 | 85.8 | 50.8 | 65.1 | 58.8 | 219.8 | 211.3 | 211.3 | YES
2 | OK | 9 | 10 | 33 | 9 | 130.5 | 3.72 | 50 | 85.8 | 50.8 | 71 | 58.8 | 219.8 | 211.3 | 211.3 | YES
3 | OK | 10 | 11 | 21 | 9 | 153.6 | 2.63 | 50 | 85.8 | 50.8 | 75.3 | 56.8 | 219.2 | 216.7 | 216.7 | YES
4 | ** OPTIMAL ** | 11 | 22 | 21 | 9 | 153.6 | 2.48 | 50 | 85.8 | 50.8 | 75.9 | 56.5 | 219 | 217.4 | 217.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 56-004479
TR_B (available) | 45-030841
TR_A Rated kVA | 30
TR_B Rated kVA | 50
TR_A Baseline Loading% | 85.8
TR_B Baseline Loading% | 50.8
Total Scenarios Evaluated | 11
Feasible Scenarios | 4
--- Optimal Solution ---
Switch Parent Node | 11
Switch Child Node | 22
Tie Node (TR_A side) | 21
Tie Node (TR_B side) | 9
Tie Line Distance (m) | 153.6
Load Transferred (kW) | 2.48
TR_A Loading After (%) | 75.9
TR_B Loading After (%) | 56.5
Minimum Voltage (V) | 217.4