## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 10 | 35 | 11 | 87 | 102.2 | 21.33 | 50 | 93.6 | 12.1 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 35 | 7 | 11 | 87 | 102.2 | 20.83 | 50 | 93.6 | 12.1 | 12.1 | 12.1 | 229.6 | 218.6 | 218.6 | YES
2 | OK | 7 | 8 | 11 | 87 | 102.2 | 20.83 | 50 | 93.6 | 12.1 | 12.1 | 12.1 | 229.6 | 218.6 | 218.6 | YES
3 | OK | 8 | 2 | 15 | 48 | 135.6 | 18.2 | 50 | 93.6 | 12.1 | 22.1 | 12.1 | 228.3 | 218.6 | 218.6 | YES
4 | OK | 2 | 3 | 15 | 48 | 135.6 | 16.32 | 50 | 93.6 | 12.1 | 29.3 | 12.1 | 226.6 | 218.6 | 218.6 | YES
5 | ** OPTIMAL ** | 3 | 32 | 15 | 48 | 135.6 | 15.61 | 50 | 93.6 | 12.1 | 32 | 12.1 | 225.9 | 218.6 | 218.6 | YES
6 | OK | 32 | 0 | 15 | 48 | 135.6 | 8.21 | 50 | 93.6 | 12.1 | 61.1 | 12.1 | 215.7 | 218.6 | 215.7 | YES
7 | OK | 0 | 1 | 15 | 48 | 135.6 | 8.06 | 50 | 93.6 | 12.1 | 61.7 | 12.1 | 215.5 | 218.6 | 215.5 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 56-004886
TR_B (available) | 29-011180
TR_A Rated kVA | 30
TR_B Rated kVA | 160
TR_A Baseline Loading% | 93.6
TR_B Baseline Loading% | 12.1
Total Scenarios Evaluated | 8
Feasible Scenarios | 7
--- Optimal Solution ---
Switch Parent Node | 3
Switch Child Node | 32
Tie Node (TR_A side) | 15
Tie Node (TR_B side) | 48
Tie Line Distance (m) | 135.6
Load Transferred (kW) | 15.61
TR_A Loading After (%) | 32
TR_B Loading After (%) | 12.1
Minimum Voltage (V) | 218.6