## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 32 | 12 | 41 | 4 | 1.8 | 9.56 | 50 | 69 | 37.5 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 12 | 13 | 41 | 4 | 1.8 | 8.01 | 50 | 69 | 37.5 | 36.8 | 44.5 | 215.6 | 189 | 189 | NO
| NG | 13 | 14 | 41 | 4 | 1.8 | 8.01 | 50 | 69 | 37.5 | 36.8 | 44.5 | 215.6 | 189 | 189 | NO
| NG | 14 | 17 | 41 | 4 | 1.8 | 8.01 | 50 | 69 | 37.5 | 36.8 | 44.5 | 215.6 | 189 | 189 | NO
| NG | 17 | 19 | 41 | 4 | 1.8 | 6.84 | 50 | 69 | 37.5 | 41.3 | 43.3 | 215.6 | 193.8 | 193.8 | NO
1 | OK | 19 | 28 | 41 | 4 | 1.8 | 2.88 | 50 | 69 | 37.5 | 57.1 | 39.8 | 215.2 | 213.2 | 213.2 | YES
2 | ** OPTIMAL ** | 28 | 48 | 41 | 4 | 1.8 | 2.54 | 50 | 69 | 37.5 | 58.5 | 39.5 | 214.5 | 213.5 | 213.5 | YES
3 | OK | 48 | 26 | 41 | 4 | 1.8 | 1.52 | 50 | 69 | 37.5 | 62.6 | 38.7 | 212.5 | 213.5 | 212.5 | YES
4 | OK | 26 | 27 | 41 | 4 | 1.8 | 1.16 | 50 | 69 | 37.5 | 64.1 | 38.4 | 211.7 | 213.5 | 211.7 | YES
5 | OK | 27 | 46 | 41 | 4 | 1.8 | 0.44 | 50 | 69 | 37.5 | 67.1 | 37.8 | 210.2 | 213.5 | 210.2 | YES
| NG | 46 | 47 | 47 | 4 | 139.1 | 0.11 | 50 | 69 | 37.5 | 68.5 | 37.6 | 209.5 | 213.5 | 209.5 | NO
6 | OK | 46 | 45 | 41 | 4 | 1.8 | 0.33 | 50 | 69 | 37.5 | 67.6 | 37.7 | 210 | 213.5 | 210 | YES
| NG | 45 | 40 | 41 | 4 | 1.8 | 0.01 | 50 | 69 | 37.5 | 68.9 | 37.5 | 209.3 | 213.5 | 209.3 | NO
| NG | 45 | 49 | 49 | 4 | 110.7 | 0.32 | 50 | 69 | 37.5 | 67.6 | 37.7 | 210 | 213.5 | 210 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 56-005447
TR_B (available) | 59-005540
TR_A Rated kVA | 30
TR_B Rated kVA | 160
TR_A Baseline Loading% | 69
TR_B Baseline Loading% | 37.5
Total Scenarios Evaluated | 14
Feasible Scenarios | 6
--- Optimal Solution ---
Switch Parent Node | 28
Switch Child Node | 48
Tie Node (TR_A side) | 41
Tie Node (TR_B side) | 4
Tie Line Distance (m) | 1.8
Load Transferred (kW) | 2.54
TR_A Loading After (%) | 58.5
TR_B Loading After (%) | 39.5
Minimum Voltage (V) | 213.5