## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 32 | 34 | 16 | 4 | 3.8 | 7.82 | 50 | 69 | 12.6 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 34 | 30 | 16 | 4 | 3.8 | 7.82 | 50 | 69 | 12.6 | 38 | 35.4 | 211.1 | 208.6 | 208.6 | NO
| NG | 30 | 15 | 16 | 4 | 3.8 | 7.82 | 50 | 69 | 12.6 | 38 | 35.4 | 211.1 | 208.6 | 208.6 | NO
1 | OK | 15 | 16 | 16 | 4 | 3.8 | 7.02 | 50 | 69 | 12.6 | 41.1 | 32 | 211.1 | 210.5 | 210.5 | YES
2 | OK | 16 | 8 | 8 | 4 | 25.6 | 7.02 | 50 | 69 | 12.6 | 41.1 | 32 | 211.1 | 210.5 | 210.5 | YES
3 | OK | 8 | 5 | 5 | 4 | 94.7 | 6.89 | 50 | 69 | 12.6 | 41.6 | 31.5 | 211.1 | 210.9 | 210.9 | YES
| NG | 5 | 4 | 43 | 16 | 99.3 | 6.78 | 50 | 69 | 12.6 | 42 | 31.8 | 211.1 | 207.3 | 207.3 | NO
4 | OK | 4 | 2 | 43 | 16 | 99.3 | 6.04 | 50 | 69 | 12.6 | 44.9 | 28.5 | 211.1 | 210.9 | 210.9 | YES
5 | OK | 2 | 3 | 43 | 16 | 99.3 | 5.03 | 50 | 69 | 12.6 | 48.8 | 24.2 | 211.1 | 215.2 | 211.1 | YES
6 | ** OPTIMAL ** | 3 | 9 | 43 | 16 | 99.3 | 5.03 | 50 | 69 | 12.6 | 48.8 | 23.2 | 211.1 | 216.1 | 211.1 | YES
7 | OK | 9 | 20 | 43 | 16 | 99.3 | 3.68 | 50 | 69 | 12.6 | 54.1 | 21.8 | 210.4 | 217.4 | 210.4 | YES
8 | OK | 20 | 44 | 43 | 16 | 99.3 | 1.7 | 50 | 69 | 12.6 | 62.1 | 14.9 | 210.2 | 224.7 | 210.2 | YES
9 | OK | 44 | 25 | 43 | 16 | 99.3 | 1.7 | 50 | 69 | 12.6 | 62.1 | 14.9 | 210.2 | 224.7 | 210.2 | YES
10 | OK | 25 | 23 | 43 | 16 | 99.3 | 1.36 | 50 | 69 | 12.6 | 63.5 | 13.5 | 210.2 | 225.8 | 210.2 | YES
11 | OK | 23 | 24 | 43 | 16 | 99.3 | 1.25 | 50 | 69 | 12.6 | 64 | 13.5 | 210.1 | 225.8 | 210.1 | YES
| NG | 24 | 42 | 43 | 16 | 99.3 | 0.11 | 50 | 69 | 12.6 | 68.5 | 13 | 209.3 | 226.1 | 209.3 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 56-005447
TR_B (available) | 65-003297
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 69
TR_B Baseline Loading% | 12.6
Total Scenarios Evaluated | 16
Feasible Scenarios | 11
--- Optimal Solution ---
Switch Parent Node | 3
Switch Child Node | 9
Tie Node (TR_A side) | 43
Tie Node (TR_B side) | 16
Tie Line Distance (m) | 99.3
Load Transferred (kW) | 5.03
TR_A Loading After (%) | 48.8
TR_B Loading After (%) | 23.2
Minimum Voltage (V) | 211.1