## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 19 | 11 | 11 | 0 | 22.4 | 8.66 | 50 | 97.2 | 40.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 19 | 9 | 54 | 2 | 13.5 | 32.94 | 50 | 97.2 | 40.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 11 | 10 | 10 | 0 | 26.3 | 8.66 | 50 | 97.2 | 40.7 | 60.7 | 44.8 | 46.2 | 216.6 | 46.2 | NO
1 | OK | 9 | 8 | 7 | 1 | 22 | 9.4 | 50 | 97.2 | 40.7 | 75.4 | 45.1 | 213.2 | 220.7 | 213.2 | YES
| NG | 9 | 45 | 54 | 2 | 13.5 | 23.54 | 50 | 97.2 | 40.7 | 41.9 | 48.7 | 220.2 | 208.7 | 208.7 | NO
| NG | 10 | 6 | 21 | 0 | 28.9 | 8.66 | 50 | 97.2 | 40.7 | 60.7 | 44.9 | 46.2 | 216.1 | 46.2 | NO
2 | OK | 8 | 7 | 7 | 1 | 22 | 9.19 | 50 | 97.2 | 40.7 | 75.9 | 45 | 213.1 | 220.9 | 213.1 | YES
| NG | 45 | 43 | 54 | 2 | 13.5 | 23.54 | 50 | 97.2 | 40.7 | 41.9 | 48.7 | 220.2 | 208.7 | 208.7 | NO
3 | OK | 7 | 25 | 25 | 1 | 22.3 | 9.19 | 50 | 97.2 | 40.7 | 75.9 | 45 | 213.1 | 220.9 | 213.1 | YES
| NG | 43 | 22 | 54 | 2 | 13.5 | 23.54 | 50 | 97.2 | 40.7 | 41.9 | 48.7 | 220.2 | 208.7 | 208.7 | NO
4 | OK | 25 | 48 | 48 | 11 | 41.2 | 9.19 | 50 | 97.2 | 40.7 | 75.9 | 45 | 213.1 | 221.1 | 213.1 | YES
5 | ** OPTIMAL ** | 22 | 0 | 54 | 2 | 13.5 | 13.66 | 50 | 97.2 | 40.7 | 64.6 | 44.5 | 214.8 | 221.1 | 214.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 56-009256
TR_B (available) | 24-005553
TR_A Rated kVA | 50
TR_B Rated kVA | 250
TR_A Baseline Loading% | 97.2
TR_B Baseline Loading% | 40.7
Total Scenarios Evaluated | 12
Feasible Scenarios | 5
--- Optimal Solution ---
Switch Parent Node | 22
Switch Child Node | 0
Tie Node (TR_A side) | 54
Tie Node (TR_B side) | 2
Tie Line Distance (m) | 13.5
Load Transferred (kW) | 13.66
TR_A Loading After (%) | 64.6
TR_B Loading After (%) | 44.5
Minimum Voltage (V) | 214.8