## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 19 | 11 | 5 | 32 | 5.3 | 8.66 | 50 | 97.2 | 42.3 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 19 | 9 | 43 | 32 | 3.5 | 32.94 | 50 | 97.2 | 42.3 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 11 | 10 | 5 | 32 | 5.3 | 8.66 | 50 | 97.2 | 42.3 | 60.7 | 53 | 46.2 | 208.4 | 46.2 | NO
1 | OK | 9 | 8 | 8 | 32 | 53.4 | 9.4 | 50 | 97.2 | 42.3 | 75.4 | 53.8 | 213.2 | 212.6 | 212.6 | YES
| NG | 9 | 45 | 43 | 32 | 3.5 | 23.54 | 50 | 97.2 | 42.3 | 41.9 | 64.7 | 220.2 | 186.2 | 186.2 | NO
| NG | 10 | 6 | 5 | 32 | 5.3 | 8.66 | 50 | 97.2 | 42.3 | 60.7 | 53 | 46.2 | 208.4 | 46.2 | NO
2 | ** OPTIMAL ** | 8 | 7 | 7 | 32 | 73.9 | 9.19 | 50 | 97.2 | 42.3 | 75.9 | 53.6 | 213.1 | 212.8 | 212.8 | YES
| NG | 45 | 43 | 43 | 32 | 3.5 | 23.54 | 50 | 97.2 | 42.3 | 41.9 | 64.7 | 220.2 | 186.2 | 186.2 | NO
3 | OK | 7 | 25 | 25 | 32 | 76 | 9.19 | 50 | 97.2 | 42.3 | 75.9 | 53.6 | 213.1 | 212.8 | 212.8 | YES
| NG | 43 | 22 | 22 | 32 | 60 | 23.54 | 50 | 97.2 | 42.3 | 41.9 | 64.7 | 220.2 | 186 | 186 | NO
4 | OK | 25 | 48 | 48 | 32 | 129 | 9.19 | 50 | 97.2 | 42.3 | 75.9 | 53.6 | 213.1 | 212.8 | 212.8 | YES
| NG | 22 | 0 | 0 | 32 | 88.1 | 13.66 | 50 | 97.2 | 42.3 | 64.6 | 59.2 | 214.8 | 207 | 207 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 56-009256
TR_B (available) | 44-005574
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 97.2
TR_B Baseline Loading% | 42.3
Total Scenarios Evaluated | 12
Feasible Scenarios | 4
--- Optimal Solution ---
Switch Parent Node | 8
Switch Child Node | 7
Tie Node (TR_A side) | 7
Tie Node (TR_B side) | 32
Tie Line Distance (m) | 73.9
Load Transferred (kW) | 9.19
TR_A Loading After (%) | 75.9
TR_B Loading After (%) | 53.6
Minimum Voltage (V) | 212.8