## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 19 | 9 | 60 | 38 | 36.5 | 32.94 | 50 | 97.2 | 25.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 9 | 45 | 60 | 38 | 36.5 | 23.54 | 50 | 97.2 | 25.8 | 41.9 | 39.7 | 220.2 | 188.2 | 188.2 | NO
| NG | 45 | 43 | 60 | 38 | 36.5 | 23.54 | 50 | 97.2 | 25.8 | 41.9 | 39.7 | 220.2 | 188.2 | 188.2 | NO
| NG | 43 | 22 | 60 | 38 | 36.5 | 23.54 | 50 | 97.2 | 25.8 | 41.9 | 39.7 | 220.2 | 188.2 | 188.2 | NO
1 | ** OPTIMAL ** | 22 | 0 | 60 | 38 | 36.5 | 13.66 | 50 | 97.2 | 25.8 | 64.6 | 32.1 | 214.8 | 210.6 | 210.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 56-009256
TR_B (available) | 56-002140
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 97.2
TR_B Baseline Loading% | 25.8
Total Scenarios Evaluated | 5
Feasible Scenarios | 1
--- Optimal Solution ---
Switch Parent Node | 22
Switch Child Node | 0
Tie Node (TR_A side) | 60
Tie Node (TR_B side) | 38
Tie Line Distance (m) | 36.5
Load Transferred (kW) | 13.66
TR_A Loading After (%) | 64.6
TR_B Loading After (%) | 32.1
Minimum Voltage (V) | 210.6