## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 19 | 11 | 11 | 13 | 97.1 | 8.66 | 50 | 97.2 | 10 | 60.7 | 20.3 | 46.2 | 217.3 | 46.2 | NO
| NG | 19 | 9 | 58 | 2 | 7 | 32.94 | 50 | 97.2 | 10 | 20.1 | 42.1 | 222.2 | 195.1 | 195.1 | NO
| NG | 11 | 10 | 10 | 13 | 112.5 | 8.66 | 50 | 97.2 | 10 | 60.7 | 20.3 | 46.2 | 217.3 | 46.2 | NO
1 | ** OPTIMAL ** | 9 | 8 | 58 | 2 | 7 | 9.4 | 50 | 97.2 | 10 | 75.4 | 20.8 | 213.2 | 228 | 213.2 | YES
| NG | 9 | 45 | 45 | 13 | 95.3 | 23.54 | 50 | 97.2 | 10 | 41.9 | 30.7 | 220.2 | 202.1 | 202.1 | NO
| NG | 10 | 6 | 6 | 13 | 119.4 | 8.66 | 50 | 97.2 | 10 | 60.7 | 20.3 | 46.2 | 217.3 | 46.2 | NO
2 | OK | 8 | 7 | 58 | 2 | 7 | 9.19 | 50 | 97.2 | 10 | 75.9 | 20.6 | 213.1 | 228.1 | 213.1 | YES
| NG | 45 | 43 | 43 | 13 | 129 | 23.54 | 50 | 97.2 | 10 | 41.9 | 30.7 | 220.2 | 201.9 | 201.9 | NO
3 | OK | 7 | 25 | 58 | 2 | 7 | 9.19 | 50 | 97.2 | 10 | 75.9 | 20.6 | 213.1 | 228.1 | 213.1 | YES
4 | OK | 25 | 48 | 58 | 2 | 7 | 9.19 | 50 | 97.2 | 10 | 75.9 | 20.6 | 213.1 | 228.1 | 213.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 56-009256
TR_B (available) | 59-019973
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 97.2
TR_B Baseline Loading% | 10
Total Scenarios Evaluated | 10
Feasible Scenarios | 4
--- Optimal Solution ---
Switch Parent Node | 9
Switch Child Node | 8
Tie Node (TR_A side) | 58
Tie Node (TR_B side) | 2
Tie Line Distance (m) | 7
Load Transferred (kW) | 9.4
TR_A Loading After (%) | 75.4
TR_B Loading After (%) | 20.8
Minimum Voltage (V) | 213.2