## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 19 | 11 | 17 | 34 | 131.6 | 8.66 | 50 | 97.2 | 18.9 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 19 | 9 | 70 | 6 | 71.1 | 32.94 | 50 | 97.2 | 18.9 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 11 | 10 | 17 | 34 | 131.6 | 8.66 | 50 | 97.2 | 18.9 | 60.7 | 22.5 | 46.2 | 219.3 | 46.2 | NO
1 | ** OPTIMAL ** | 9 | 8 | 70 | 6 | 71.1 | 9.4 | 50 | 97.2 | 18.9 | 75.4 | 23.4 | 213.2 | 223.5 | 213.2 | YES
| NG | 9 | 45 | 44 | 39 | 140.5 | 23.54 | 50 | 97.2 | 18.9 | 41.9 | 27.7 | 220.2 | 193.3 | 193.3 | NO
| NG | 10 | 6 | 17 | 34 | 131.6 | 8.66 | 50 | 97.2 | 18.9 | 60.7 | 22.5 | 46.2 | 219.3 | 46.2 | NO
2 | OK | 8 | 7 | 70 | 6 | 71.1 | 9.19 | 50 | 97.2 | 18.9 | 75.9 | 23.3 | 213.1 | 223.5 | 213.1 | YES
| NG | 45 | 43 | 44 | 39 | 140.5 | 23.54 | 50 | 97.2 | 18.9 | 41.9 | 27.7 | 220.2 | 193.3 | 193.3 | NO
3 | OK | 7 | 25 | 70 | 6 | 71.1 | 9.19 | 50 | 97.2 | 18.9 | 75.9 | 23.3 | 213.1 | 223.5 | 213.1 | YES
4 | OK | 25 | 48 | 70 | 6 | 71.1 | 9.19 | 50 | 97.2 | 18.9 | 75.9 | 23.3 | 213.1 | 223.5 | 213.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 56-009256
TR_B (available) | 59-025149
TR_A Rated kVA | 50
TR_B Rated kVA | 250
TR_A Baseline Loading% | 97.2
TR_B Baseline Loading% | 18.9
Total Scenarios Evaluated | 10
Feasible Scenarios | 4
--- Optimal Solution ---
Switch Parent Node | 9
Switch Child Node | 8
Tie Node (TR_A side) | 70
Tie Node (TR_B side) | 6
Tie Line Distance (m) | 71.1
Load Transferred (kW) | 9.4
TR_A Loading After (%) | 75.4
TR_B Loading After (%) | 23.4
Minimum Voltage (V) | 213.2