## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 8 | 9 | 14 | 0 | 30.5 | 7.46 | 50 | 90.5 | 60.8 | 73.1 | 70.4 | 209.9 | 216.1 | 209.9 | NO
1 | OK | 9 | 6 | 14 | 0 | 30.5 | 5.56 | 50 | 90.5 | 60.8 | 77.5 | 67 | 210 | 219.8 | 210 | YES
2 | OK | 6 | 7 | 14 | 0 | 30.5 | 5.56 | 50 | 90.5 | 60.8 | 77.5 | 67 | 210 | 219.8 | 210 | YES
3 | OK | 7 | 17 | 14 | 0 | 30.5 | 5.56 | 50 | 90.5 | 60.8 | 77.5 | 67 | 210 | 219.8 | 210 | YES
4 | OK | 17 | 4 | 14 | 0 | 30.5 | 5.56 | 50 | 90.5 | 60.8 | 77.5 | 67 | 210 | 219.8 | 210 | YES
5 | ** OPTIMAL ** | 4 | 5 | 14 | 0 | 30.5 | 5.56 | 50 | 90.5 | 60.8 | 77.5 | 67 | 210 | 219.8 | 210 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 56-009260
TR_B (available) | 55-940577
TR_A Rated kVA | 50
TR_B Rated kVA | 50
TR_A Baseline Loading% | 90.5
TR_B Baseline Loading% | 60.8
Total Scenarios Evaluated | 6
Feasible Scenarios | 5
--- Optimal Solution ---
Switch Parent Node | 4
Switch Child Node | 5
Tie Node (TR_A side) | 14
Tie Node (TR_B side) | 0
Tie Line Distance (m) | 30.5
Load Transferred (kW) | 5.56
TR_A Loading After (%) | 77.5
TR_B Loading After (%) | 67
Minimum Voltage (V) | 210