## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 8 | 9 | 9 | 17 | 140.8 | 7.46 | 50 | 90.5 | 38.7 | 73.1 | 56.2 | 209.9 | 220 | 209.9 | NO
| NG | 8 | 15 | 15 | 17 | 109.5 | 16.93 | 50 | 90.5 | 38.7 | 50 | 80.5 | 216.6 | 203.1 | 203.1 | NO
1 | OK | 9 | 6 | 6 | 17 | 148.1 | 5.56 | 50 | 90.5 | 38.7 | 77.5 | 51.7 | 210 | 220.4 | 210 | YES
| NG | 15 | 16 | 16 | 17 | 113.7 | 15.5 | 50 | 90.5 | 38.7 | 53.3 | 76.6 | 216.7 | 206.3 | 206.3 | NO
2 | ** OPTIMAL ** | 16 | 20 | 20 | 17 | 116 | 11.62 | 50 | 90.5 | 38.7 | 62.2 | 66.6 | 217.2 | 212.1 | 212.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 56-009260
TR_B (available) | 61-008797
TR_A Rated kVA | 50
TR_B Rated kVA | 50
TR_A Baseline Loading% | 90.5
TR_B Baseline Loading% | 38.7
Total Scenarios Evaluated | 5
Feasible Scenarios | 2
--- Optimal Solution ---
Switch Parent Node | 16
Switch Child Node | 20
Tie Node (TR_A side) | 20
Tie Node (TR_B side) | 17
Tie Line Distance (m) | 116
Load Transferred (kW) | 11.62
TR_A Loading After (%) | 62.2
TR_B Loading After (%) | 66.6
Minimum Voltage (V) | 212.1