## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 10 | 11 | 0 | 0 | 3.8 | 37.67 | 50 | 90.5 | 20.1 | 1.7 | 49.2 | 230.7 | 201.1 | 201.1 | NO
| NG | 11 | 18 | 0 | 0 | 3.8 | 35.24 | 50 | 90.5 | 20.1 | 7.3 | 47.2 | 229.9 | 203.3 | 203.3 | NO
| NG | 18 | 19 | 0 | 0 | 3.8 | 34.6 | 50 | 90.5 | 20.1 | 8.7 | 45.8 | 229.5 | 203.7 | 203.7 | NO
| NG | 19 | 23 | 0 | 0 | 3.8 | 33.43 | 50 | 90.5 | 20.1 | 11.4 | 45.8 | 229.5 | 203.7 | 203.7 | NO
| NG | 23 | 24 | 0 | 0 | 3.8 | 33.43 | 50 | 90.5 | 20.1 | 11.4 | 240 | 229.5 | 23.8 | 23.8 | NO
| NG | 24 | 27 | 0 | 0 | 3.8 | 24.7 | 50 | 90.5 | 20.1 | 31.7 | 39.3 | 222.4 | 203.2 | 203.2 | NO
| NG | 27 | 8 | 0 | 0 | 3.8 | 24.7 | 50 | 90.5 | 20.1 | 31.7 | 39 | 222.5 | 203.7 | 203.7 | NO
| NG | 8 | 9 | 0 | 0 | 3.8 | 7.46 | 50 | 90.5 | 20.1 | 73.1 | 25.5 | 209.9 | 220 | 209.9 | NO
| NG | 8 | 15 | 15 | 14 | 110.9 | 16.93 | 50 | 90.5 | 20.1 | 50 | 33.6 | 216.6 | 205.8 | 205.8 | NO
1 | OK | 9 | 6 | 0 | 0 | 3.8 | 5.56 | 50 | 90.5 | 20.1 | 77.5 | 24.2 | 210 | 220.1 | 210 | YES
| NG | 15 | 16 | 16 | 14 | 125.4 | 15.5 | 50 | 90.5 | 20.1 | 53.3 | 32.3 | 216.7 | 208.2 | 208.2 | NO
2 | OK | 6 | 7 | 0 | 0 | 3.8 | 5.56 | 50 | 90.5 | 20.1 | 77.5 | 24.2 | 210 | 220.1 | 210 | YES
3 | ** OPTIMAL ** | 16 | 20 | 20 | 14 | 130.7 | 11.62 | 50 | 90.5 | 20.1 | 62.2 | 29.1 | 217.2 | 213.9 | 213.9 | YES
4 | OK | 7 | 17 | 0 | 0 | 3.8 | 5.56 | 50 | 90.5 | 20.1 | 77.5 | 24.2 | 210 | 220.1 | 210 | YES
5 | OK | 17 | 4 | 0 | 0 | 3.8 | 5.56 | 50 | 90.5 | 20.1 | 77.5 | 24.2 | 210 | 220.1 | 210 | YES
6 | OK | 4 | 5 | 0 | 0 | 3.8 | 5.56 | 50 | 90.5 | 20.1 | 77.5 | 24.2 | 210 | 220.1 | 210 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 56-009260
TR_B (available) | 63-005636
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 90.5
TR_B Baseline Loading% | 20.1
Total Scenarios Evaluated | 16
Feasible Scenarios | 6
--- Optimal Solution ---
Switch Parent Node | 16
Switch Child Node | 20
Tie Node (TR_A side) | 20
Tie Node (TR_B side) | 14
Tie Line Distance (m) | 130.7
Load Transferred (kW) | 11.62
TR_A Loading After (%) | 62.2
TR_B Loading After (%) | 29.1
Minimum Voltage (V) | 213.9