## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 26 | 25 | 0 | 48 | 1.3 | 17.82 | 95 | 81.3 | 27.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | ** OPTIMAL ** | 25 | 5 | 0 | 48 | 1.3 | 17.82 | 95 | 81.3 | 27.2 | 40 | 40.2 | 212.4 | 214.2 | 212.4 | YES
2 | OK | 5 | 4 | 0 | 48 | 1.3 | 17.01 | 95 | 81.3 | 27.2 | 41.9 | 39.6 | 212 | 214.2 | 212 | YES
3 | OK | 4 | 12 | 0 | 48 | 1.3 | 14.07 | 95 | 81.3 | 27.2 | 48.6 | 37.4 | 212 | 214.3 | 212 | YES
4 | OK | 12 | 9 | 0 | 48 | 1.3 | 12.94 | 95 | 81.3 | 27.2 | 51.2 | 36.6 | 212 | 214.4 | 212 | YES
5 | OK | 9 | 8 | 0 | 48 | 1.3 | 11.26 | 95 | 81.3 | 27.2 | 53.2 | 35.4 | 212 | 214.5 | 212 | YES
6 | OK | 9 | 10 | 11 | 9 | 96.8 | 0.88 | 50 | 81.3 | 27.2 | 79.3 | 27.9 | 212 | 215 | 212 | YES
7 | OK | 8 | 20 | 0 | 48 | 1.3 | 11.26 | 95 | 81.3 | 27.2 | 53.2 | 35.4 | 212 | 214.5 | 212 | YES
8 | OK | 20 | 19 | 0 | 48 | 1.3 | 11.26 | 95 | 81.3 | 27.2 | 55.1 | 35.4 | 212 | 214.5 | 212 | YES
9 | OK | 19 | 39 | 0 | 48 | 1.3 | 11.26 | 95 | 81.3 | 27.2 | 55.1 | 35.4 | 212 | 214.5 | 212 | YES
10 | OK | 39 | 18 | 0 | 48 | 1.3 | 11.15 | 95 | 81.3 | 27.2 | 55.3 | 35.3 | 212 | 214.5 | 212 | YES
11 | OK | 18 | 3 | 0 | 48 | 1.3 | 7.89 | 95 | 81.3 | 27.2 | 58.3 | 32.9 | 212 | 214.8 | 212 | YES
12 | OK | 18 | 34 | 34 | 48 | 80.9 | 0.93 | 50 | 81.3 | 27.2 | 79.1 | 27.9 | 212 | 215.7 | 212 | YES
13 | OK | 3 | 2 | 0 | 48 | 1.3 | 7.89 | 95 | 81.3 | 27.2 | 58.5 | 32.9 | 212 | 214.8 | 212 | YES
14 | OK | 2 | 28 | 0 | 48 | 1.3 | 7.78 | 95 | 81.3 | 27.2 | 63.1 | 30.6 | 212 | 215.4 | 212 | YES
15 | OK | 28 | 1 | 0 | 48 | 1.3 | 2.9 | 95 | 81.3 | 27.2 | 74.5 | 29.3 | 212 | 215.4 | 212 | YES
16 | OK | 28 | 31 | 29 | 48 | 30.8 | 4.88 | 50 | 81.3 | 27.2 | 69.9 | 28.5 | 212 | 215.7 | 212 | YES
17 | OK | 1 | 0 | 0 | 48 | 1.3 | 2.14 | 95 | 81.3 | 27.2 | 76.3 | 28.8 | 212 | 215.4 | 212 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 56-010196
TR_B (available) | 56-002469
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 81.3
TR_B Baseline Loading% | 27.2
Total Scenarios Evaluated | 18
Feasible Scenarios | 17
--- Optimal Solution ---
Switch Parent Node | 25
Switch Child Node | 5
Tie Node (TR_A side) | 0
Tie Node (TR_B side) | 48
Tie Line Distance (m) | 1.3
Load Transferred (kW) | 17.82
TR_A Loading After (%) | 40
TR_B Loading After (%) | 40.2
Minimum Voltage (V) | 212.4