## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 26 | 25 | 31 | 9 | 40.4 | 17.82 | 50 | 81.3 | 37.4 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 26 | 27 | 27 | 37 | 43.3 | 16.86 | 50 | 81.3 | 37.4 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 25 | 5 | 31 | 9 | 40.4 | 17.82 | 50 | 81.3 | 37.4 | 40 | 57.3 | 212.4 | 214.8 | 212.4 | YES
| NG | 27 | 13 | 13 | 42 | 45.3 | 16.67 | 50 | 81.3 | 37.4 | 41.7 | 59.1 | 222.2 | 193.1 | 193.1 | NO
2 | OK | 5 | 4 | 31 | 9 | 40.4 | 17.01 | 50 | 81.3 | 37.4 | 41.9 | 57.2 | 212 | 214.8 | 212 | YES
| NG | 13 | 14 | 14 | 2 | 46.8 | 14.27 | 50 | 81.3 | 37.4 | 47.2 | 56 | 222.2 | 194.8 | 194.8 | NO
3 | OK | 4 | 6 | 6 | 4 | 45.7 | 2.94 | 50 | 81.3 | 37.4 | 74.6 | 40.8 | 212 | 216.4 | 212 | YES
4 | OK | 4 | 12 | 31 | 9 | 40.4 | 14.07 | 50 | 81.3 | 37.4 | 48.6 | 53.7 | 212 | 215 | 212 | YES
| NG | 14 | 37 | 36 | 0 | 80.5 | 13.22 | 50 | 81.3 | 37.4 | 49.6 | 50.9 | 222.2 | 196.9 | 196.9 | NO
5 | OK | 6 | 7 | 7 | 4 | 47 | 2.94 | 50 | 81.3 | 37.4 | 74.6 | 37.4 | 212 | 216.6 | 212 | YES
6 | OK | 12 | 9 | 31 | 9 | 40.4 | 12.94 | 50 | 81.3 | 37.4 | 51.2 | 52.4 | 212 | 215 | 212 | YES
7 | ** OPTIMAL ** | 37 | 36 | 36 | 0 | 80.5 | 2.16 | 50 | 81.3 | 37.4 | 76 | 40 | 214.9 | 216.7 | 214.9 | YES
| NG | 37 | 42 | 42 | 0 | 140.6 | 11.06 | 50 | 81.3 | 37.4 | 54.6 | 51.5 | 222.2 | 201.6 | 201.6 | NO
8 | OK | 9 | 8 | 31 | 9 | 40.4 | 11.26 | 50 | 81.3 | 37.4 | 53.2 | 50.4 | 212 | 215.2 | 212 | YES
9 | OK | 9 | 10 | 10 | 7 | 120 | 0.88 | 50 | 81.3 | 37.4 | 79.3 | 38.4 | 212 | 216.4 | 212 | YES
10 | OK | 36 | 41 | 41 | 0 | 117.9 | 1.69 | 50 | 81.3 | 37.4 | 77.2 | 39.4 | 214.3 | 216.7 | 214.3 | YES
11 | OK | 8 | 20 | 31 | 9 | 40.4 | 11.26 | 50 | 81.3 | 37.4 | 53.2 | 50.4 | 212 | 215.2 | 212 | YES
12 | OK | 41 | 16 | 16 | 0 | 142.6 | 1.29 | 50 | 81.3 | 37.4 | 78.1 | 38.9 | 213.8 | 216.7 | 213.8 | YES
13 | OK | 20 | 19 | 31 | 9 | 40.4 | 11.26 | 50 | 81.3 | 37.4 | 55.1 | 50.4 | 212 | 215.2 | 212 | YES
14 | OK | 19 | 39 | 31 | 9 | 40.4 | 11.26 | 50 | 81.3 | 37.4 | 55.1 | 50.4 | 212 | 215.2 | 212 | YES
15 | OK | 39 | 18 | 31 | 9 | 40.4 | 11.15 | 50 | 81.3 | 37.4 | 55.3 | 50.3 | 212 | 215.2 | 212 | YES
16 | OK | 18 | 3 | 31 | 9 | 40.4 | 7.89 | 50 | 81.3 | 37.4 | 58.3 | 46.5 | 212 | 215.6 | 212 | YES
17 | OK | 18 | 34 | 34 | 39 | 45.9 | 0.93 | 50 | 81.3 | 37.4 | 79.1 | 38.4 | 212 | 216.6 | 212 | YES
18 | OK | 3 | 2 | 31 | 9 | 40.4 | 7.89 | 50 | 81.3 | 37.4 | 58.5 | 46.5 | 212 | 215.6 | 212 | YES
19 | OK | 2 | 28 | 31 | 9 | 40.4 | 7.78 | 50 | 81.3 | 37.4 | 63.1 | 42.7 | 212 | 216.3 | 212 | YES
20 | OK | 28 | 1 | 1 | 10 | 42.4 | 2.9 | 50 | 81.3 | 37.4 | 74.5 | 40.7 | 212 | 216.3 | 212 | YES
21 | OK | 28 | 31 | 31 | 9 | 40.4 | 4.88 | 50 | 81.3 | 37.4 | 69.9 | 39.3 | 212 | 216.6 | 212 | YES
22 | OK | 1 | 0 | 0 | 11 | 42.8 | 2.14 | 50 | 81.3 | 37.4 | 76.3 | 39.8 | 212 | 216.3 | 212 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 56-010196
TR_B (available) | 56-008430
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 81.3
TR_B Baseline Loading% | 37.4
Total Scenarios Evaluated | 28
Feasible Scenarios | 22
--- Optimal Solution ---
Switch Parent Node | 37
Switch Child Node | 36
Tie Node (TR_A side) | 36
Tie Node (TR_B side) | 0
Tie Line Distance (m) | 80.5
Load Transferred (kW) | 2.16
TR_A Loading After (%) | 76
TR_B Loading After (%) | 40
Minimum Voltage (V) | 214.9