## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 37 | 36 | 36 | 11 | 60.7 | 2.16 | 50 | 81.3 | 37.5 | 76 | 45.9 | 214.9 | 218.5 | 214.9 | YES
2 | ** OPTIMAL ** | 37 | 42 | 32 | 8 | 45.2 | 11.06 | 50 | 81.3 | 37.5 | 54.6 | 37.5 | 222.2 | 220.1 | 220.1 | YES
3 | OK | 36 | 41 | 41 | 1 | 117.8 | 1.69 | 50 | 81.3 | 37.5 | 77.2 | 44 | 214.3 | 218.8 | 214.3 | YES
4 | OK | 42 | 22 | 32 | 8 | 45.2 | 11.06 | 50 | 81.3 | 37.5 | 54.6 | 37.5 | 222.2 | 220.1 | 220.1 | YES
5 | OK | 41 | 16 | 16 | 1 | 142.9 | 1.29 | 50 | 81.3 | 37.5 | 78.1 | 42.5 | 213.8 | 219.1 | 213.8 | YES
6 | OK | 22 | 21 | 32 | 8 | 45.2 | 11.06 | 50 | 81.3 | 37.5 | 54.6 | 37.5 | 222.2 | 220.1 | 220.1 | YES
7 | OK | 21 | 24 | 32 | 8 | 45.2 | 11.06 | 50 | 81.3 | 37.5 | 54.6 | 37.5 | 222.2 | 220.1 | 220.1 | YES
8 | OK | 24 | 23 | 32 | 8 | 45.2 | 11.06 | 50 | 81.3 | 37.5 | 54.6 | 37.5 | 222.2 | 220.1 | 220.1 | YES
9 | OK | 23 | 32 | 32 | 8 | 45.2 | 2.84 | 50 | 81.3 | 37.5 | 74.8 | 37.5 | 210.8 | 220.1 | 210.8 | YES
10 | OK | 32 | 47 | 47 | 8 | 46.3 | 2.84 | 50 | 81.3 | 37.5 | 74.8 | 48.5 | 210.8 | 217.2 | 210.8 | YES
11 | OK | 47 | 33 | 33 | 7 | 46.3 | 2.06 | 50 | 81.3 | 37.5 | 76.6 | 45.5 | 211.1 | 217.7 | 211.1 | YES
12 | OK | 33 | 35 | 35 | 7 | 46.8 | 2.06 | 50 | 81.3 | 37.5 | 76.6 | 45.5 | 211.1 | 217.7 | 211.1 | YES
13 | OK | 35 | 46 | 43 | 6 | 47.1 | 0.83 | 50 | 81.3 | 37.5 | 79.4 | 40.7 | 211.7 | 218.6 | 211.7 | YES
14 | OK | 46 | 43 | 43 | 6 | 47.1 | 0.78 | 50 | 81.3 | 37.5 | 79.5 | 40.5 | 211.7 | 218.6 | 211.7 | YES
15 | OK | 43 | 44 | 44 | 2 | 93.4 | 0.78 | 50 | 81.3 | 37.5 | 79.5 | 40.5 | 211.7 | 218.7 | 211.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 56-010196
TR_B (available) | 63-014754
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 81.3
TR_B Baseline Loading% | 37.5
Total Scenarios Evaluated | 15
Feasible Scenarios | 15
--- Optimal Solution ---
Switch Parent Node | 37
Switch Child Node | 42
Tie Node (TR_A side) | 32
Tie Node (TR_B side) | 8
Tie Line Distance (m) | 45.2
Load Transferred (kW) | 11.06
TR_A Loading After (%) | 54.6
TR_B Loading After (%) | 37.5
Minimum Voltage (V) | 220.1