## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 62 | 23 | 82 | 34 | 88.1 | 12.75 | 50 | 85.3 | 41.2 | [5 empty] | NO | TR_B sim: not converged
| NG | 62 | 61 | 49 | 34 | 145.9 | 23.76 | 50 | 85.3 | 41.2 | [5 empty] | NO | TR_B sim: not converged
| NG | 23 | 0 | 82 | 34 | 88.1 | 12.44 | 50 | 85.3 | 41.2 | [5 empty] | NO | TR_B sim: not converged
| NG | 61 | 60 | 49 | 34 | 145.9 | 23.3 | 50 | 85.3 | 41.2 | [5 empty] | NO | TR_B sim: not converged
| NG | 0 | 1 | 82 | 34 | 88.1 | 11.55 | 50 | 85.3 | 41.2 | 58.2 | 64.2 | 215.8 | 121.3 | 121.3 | NO
| NG | 60 | 88 | 49 | 34 | 145.9 | 20.15 | 50 | 85.3 | 41.2 | [5 empty] | NO | TR_B sim: not converged
| NG | 88 | 52 | 49 | 34 | 145.9 | 20.15 | 50 | 85.3 | 41.2 | [5 empty] | NO | TR_B sim: not converged
| NG | 52 | 21 | 49 | 34 | 145.9 | 8.07 | 50 | 85.3 | 41.2 | 66.3 | 52.7 | 213.5 | 186.1 | 186.1 | NO
| NG | 21 | 22 | 49 | 34 | 145.9 | 7.69 | 50 | 85.3 | 41.2 | 67.2 | 52.1 | 213.5 | 188.2 | 188.2 | NO
| NG | 22 | 74 | 49 | 34 | 145.9 | 7.69 | 50 | 85.3 | 41.2 | 67.2 | 52.1 | 213.5 | 188.2 | 188.2 | NO
| NG | 74 | 55 | 49 | 34 | 145.9 | 7.69 | 50 | 85.3 | 41.2 | 67.2 | 52.1 | 213.5 | 188.2 | 188.2 | NO
| NG | 55 | 56 | 49 | 34 | 145.9 | 7.69 | 50 | 85.3 | 41.2 | 67.2 | 52.1 | 213.5 | 188.2 | 188.2 | NO
1 | OK | 56 | 57 | 49 | 34 | 145.9 | 2.95 | 50 | 85.3 | 41.2 | 78.4 | 45 | 213.5 | 211 | 211 | YES
2 | OK | 57 | 77 | 49 | 34 | 145.9 | 2.95 | 50 | 85.3 | 41.2 | 78.4 | 45 | 213.5 | 211 | 211 | YES
3 | ** OPTIMAL ** | 77 | 43 | 49 | 34 | 145.9 | 2.76 | 50 | 85.3 | 41.2 | 78.8 | 44.7 | 213.5 | 211.7 | 211.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 56-013842
TR_B (available) | 45-005978
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 85.3
TR_B Baseline Loading% | 41.2
Total Scenarios Evaluated | 15
Feasible Scenarios | 3
--- Optimal Solution ---
Switch Parent Node | 77
Switch Child Node | 43
Tie Node (TR_A side) | 49
Tie Node (TR_B side) | 34
Tie Line Distance (m) | 145.9
Load Transferred (kW) | 2.76
TR_A Loading After (%) | 78.8
TR_B Loading After (%) | 44.7
Minimum Voltage (V) | 211.7