## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 62 | 23 | 23 | 16 | 143.3 | 12.75 | 50 | 85.3 | 27.3 | 55.5 | 68.4 | 215.9 | 206.5 | 206.5 | NO
| NG | 23 | 0 | 0 | 16 | 181.3 | 12.44 | 50 | 85.3 | 27.3 | 56.2 | 67.2 | 215.8 | 207 | 207 | NO
| NG | 0 | 1 | 1 | 16 | 206 | 11.55 | 50 | 85.3 | 27.3 | 58.2 | 63.7 | 215.8 | 207 | 207 | NO
1 | OK | 52 | 21 | 55 | 6 | 64.2 | 8.07 | 50 | 85.3 | 27.3 | 66.3 | 35.2 | 213.5 | 222.3 | 213.5 | YES
2 | OK | 52 | 73 | 72 | 16 | 64.5 | 12.08 | 50 | 85.3 | 27.3 | 56.8 | 57.8 | 214.1 | 218.2 | 214.1 | YES
3 | OK | 21 | 22 | 55 | 6 | 64.2 | 7.69 | 50 | 85.3 | 27.3 | 67.2 | 33.8 | 213.5 | 222.3 | 213.5 | YES
4 | ** OPTIMAL ** | 73 | 72 | 72 | 16 | 64.5 | 11.82 | 50 | 85.3 | 27.3 | 56.8 | 56.8 | 214.1 | 218.2 | 214.1 | YES
5 | OK | 22 | 74 | 55 | 6 | 64.2 | 7.69 | 50 | 85.3 | 27.3 | 67.2 | 33.8 | 213.5 | 222.3 | 213.5 | YES
6 | OK | 72 | 71 | 71 | 16 | 78.6 | 11.82 | 50 | 85.3 | 27.3 | 57.4 | 56.7 | 213.9 | 219 | 213.9 | YES
7 | OK | 74 | 55 | 55 | 6 | 64.2 | 7.69 | 50 | 85.3 | 27.3 | 67.2 | 33.8 | 213.5 | 222.3 | 213.5 | YES
8 | OK | 71 | 51 | 51 | 16 | 85 | 11.69 | 50 | 85.3 | 27.3 | 57.7 | 56.2 | 213.9 | 219 | 213.9 | YES
9 | OK | 55 | 56 | 57 | 5 | 64.5 | 7.69 | 50 | 85.3 | 27.3 | 67.2 | 33.8 | 213.5 | 221.7 | 213.5 | YES
10 | OK | 51 | 14 | 14 | 16 | 113.5 | 11.39 | 50 | 85.3 | 27.3 | 58.4 | 55 | 213.8 | 219.5 | 213.8 | YES
11 | OK | 56 | 57 | 57 | 5 | 64.5 | 2.95 | 50 | 85.3 | 27.3 | 78.4 | 33.8 | 213.5 | 221.7 | 213.5 | YES
12 | OK | 14 | 13 | 13 | 16 | 125 | 7.59 | 50 | 85.3 | 27.3 | 66.9 | 40.2 | 213.9 | 222.2 | 213.9 | YES
13 | OK | 14 | 15 | 15 | 16 | 207.2 | 3.64 | 50 | 85.3 | 27.3 | 76.7 | 41.4 | 212.8 | 222.3 | 212.8 | YES
14 | OK | 57 | 77 | 77 | 4 | 65 | 2.95 | 50 | 85.3 | 27.3 | 78.4 | 33.8 | 213.5 | 221.5 | 213.5 | YES
15 | OK | 13 | 35 | 35 | 16 | 172.3 | 6.97 | 50 | 85.3 | 27.3 | 68.8 | 39.7 | 213.9 | 222.2 | 213.9 | YES
16 | OK | 77 | 43 | 44 | 3 | 65.2 | 2.76 | 50 | 85.3 | 27.3 | 78.8 | 33.1 | 213.5 | 221.2 | 213.5 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 56-013842
TR_B (available) | 59-012408
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 85.3
TR_B Baseline Loading% | 27.3
Total Scenarios Evaluated | 19
Feasible Scenarios | 16
--- Optimal Solution ---
Switch Parent Node | 73
Switch Child Node | 72
Tie Node (TR_A side) | 72
Tie Node (TR_B side) | 16
Tie Line Distance (m) | 64.5
Load Transferred (kW) | 11.82
TR_A Loading After (%) | 56.8
TR_B Loading After (%) | 56.8
Minimum Voltage (V) | 214.1