## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 52 | 21 | 21 | 19 | 71.6 | 8.07 | 50 | 85.3 | 39.1 | 66.3 | 47.2 | 213.5 | 218.3 | 213.5 | YES
2 | OK | 52 | 73 | 71 | 1 | 64 | 12.08 | 50 | 85.3 | 39.1 | 56.8 | 70.6 | 214.1 | 212.1 | 212.1 | YES
3 | OK | 21 | 22 | 22 | 19 | 86.9 | 7.69 | 50 | 85.3 | 39.1 | 67.2 | 45.8 | 213.5 | 218.3 | 213.5 | YES
4 | OK | 73 | 72 | 71 | 1 | 64 | 11.82 | 50 | 85.3 | 39.1 | 56.8 | 69.5 | 214.1 | 212 | 212 | YES
5 | OK | 22 | 74 | 74 | 19 | 91.4 | 7.69 | 50 | 85.3 | 39.1 | 67.2 | 45.8 | 213.5 | 218.3 | 213.5 | YES
6 | OK | 72 | 71 | 71 | 1 | 64 | 11.82 | 50 | 85.3 | 39.1 | 57.4 | 69.5 | 213.9 | 212 | 212 | YES
7 | OK | 74 | 55 | 55 | 19 | 102.7 | 7.69 | 50 | 85.3 | 39.1 | 67.2 | 45.8 | 213.5 | 218.3 | 213.5 | YES
8 | ** OPTIMAL ** | 71 | 51 | 35 | 18 | 64 | 11.69 | 50 | 85.3 | 39.1 | 57.7 | 68.5 | 213.9 | 214.9 | 213.9 | YES
9 | OK | 55 | 56 | 56 | 19 | 136.3 | 7.69 | 50 | 85.3 | 39.1 | 67.2 | 45.8 | 213.5 | 218.4 | 213.5 | YES
10 | OK | 51 | 14 | 35 | 18 | 64 | 11.39 | 50 | 85.3 | 39.1 | 58.4 | 67.3 | 213.8 | 215.3 | 213.8 | YES
11 | OK | 14 | 13 | 35 | 18 | 64 | 7.59 | 50 | 85.3 | 39.1 | 66.9 | 52.2 | 213.9 | 220.5 | 213.9 | YES
12 | OK | 13 | 35 | 35 | 18 | 64 | 6.97 | 50 | 85.3 | 39.1 | 68.8 | 51.7 | 213.9 | 220.5 | 213.9 | YES
13 | OK | 35 | 34 | 29 | 4 | 64.8 | 6.1 | 50 | 85.3 | 39.1 | 70.8 | 48.2 | 213.8 | 221.5 | 213.8 | YES
14 | OK | 34 | 33 | 29 | 4 | 64.8 | 4.87 | 50 | 85.3 | 39.1 | 73.6 | 44.8 | 213.4 | 222.3 | 213.4 | YES
15 | OK | 33 | 29 | 29 | 4 | 64.8 | 4.87 | 50 | 85.3 | 39.1 | 73.6 | 44.8 | 213.4 | 222.3 | 213.4 | YES
16 | OK | 29 | 28 | 26 | 13 | 65 | 3.66 | 50 | 85.3 | 39.1 | 76.5 | 40.7 | 213 | 222.9 | 213 | YES
17 | OK | 28 | 27 | 26 | 13 | 65 | 3.25 | 50 | 85.3 | 39.1 | 77.4 | 39.1 | 212.9 | 223 | 212.9 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 56-013842
TR_B (available) | 63-014867
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 85.3
TR_B Baseline Loading% | 39.1
Total Scenarios Evaluated | 17
Feasible Scenarios | 17
--- Optimal Solution ---
Switch Parent Node | 71
Switch Child Node | 51
Tie Node (TR_A side) | 35
Tie Node (TR_B side) | 18
Tie Line Distance (m) | 64
Load Transferred (kW) | 11.69
TR_A Loading After (%) | 57.7
TR_B Loading After (%) | 68.5
Minimum Voltage (V) | 213.9