## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 14 | 2 | 2 | 21 | 199.8 | 10.9 | 50 | 77.4 | 45.6 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 14 | 15 | 13 | 71 | 3 | 22.35 | 50 | 77.4 | 45.6 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 15 | 21 | 13 | 71 | 3 | 22.35 | 50 | 77.4 | 45.6 | 25.2 | 62.9 | 221.8 | 202.1 | 202.1 | NO
1 | OK | 21 | 26 | 17 | 71 | 146.5 | 7.61 | 50 | 77.4 | 45.6 | 59.5 | 51.4 | 219.8 | 210.4 | 210.4 | YES
2 | OK | 21 | 9 | 13 | 71 | 3 | 14.74 | 50 | 77.4 | 45.6 | 43 | 56.7 | 218 | 214.4 | 214.4 | YES
3 | OK | 26 | 25 | 17 | 71 | 146.5 | 7.1 | 50 | 77.4 | 45.6 | 60.7 | 51 | 219.6 | 211.5 | 211.5 | YES
4 | OK | 9 | 10 | 13 | 71 | 3 | 14.74 | 50 | 77.4 | 45.6 | 43 | 56.7 | 218 | 214.4 | 214.4 | YES
5 | ** OPTIMAL ** | 25 | 19 | 17 | 71 | 146.5 | 2.41 | 50 | 77.4 | 45.6 | 71.7 | 47.3 | 217.2 | 222.9 | 217.2 | YES
6 | OK | 10 | 11 | 13 | 71 | 3 | 13.22 | 50 | 77.4 | 45.6 | 46.6 | 55.5 | 217.2 | 213.9 | 213.9 | YES
7 | OK | 19 | 16 | 17 | 71 | 146.5 | 1.45 | 50 | 77.4 | 45.6 | 73.9 | 46.6 | 216.7 | 222.7 | 216.7 | YES
8 | OK | 11 | 22 | 13 | 71 | 3 | 12.37 | 50 | 77.4 | 45.6 | 48.6 | 54.9 | 216.8 | 213.7 | 213.7 | YES
9 | OK | 22 | 23 | 13 | 71 | 3 | 12.37 | 50 | 77.4 | 45.6 | 48.6 | 54.9 | 216.8 | 213.7 | 213.7 | YES
10 | OK | 23 | 24 | 24 | 71 | 61.4 | 6.97 | 50 | 77.4 | 45.6 | 61.1 | 50.8 | 215.8 | 215.8 | 215.8 | YES
11 | OK | 23 | 12 | 13 | 71 | 3 | 5.4 | 50 | 77.4 | 45.6 | 64.7 | 49.6 | 216.8 | 220.5 | 216.8 | YES
12 | OK | 24 | 53 | 53 | 71 | 100.8 | 6.97 | 50 | 77.4 | 45.6 | 61.1 | 50.8 | 215.8 | 215.9 | 215.8 | YES
13 | OK | 12 | 13 | 13 | 71 | 3 | 4.73 | 50 | 77.4 | 45.6 | 66.3 | 49.1 | 216.8 | 221 | 216.8 | YES
14 | OK | 53 | 60 | 60 | 75 | 128.1 | 4.77 | 50 | 77.4 | 45.6 | 66.2 | 47.7 | 215.9 | 218 | 215.9 | YES
15 | OK | 13 | 28 | 28 | 75 | 19.4 | 4.73 | 50 | 77.4 | 45.6 | 66.3 | 46.6 | 216.8 | 220.5 | 216.8 | YES
16 | OK | 60 | 5 | 5 | 75 | 132.9 | 4.77 | 50 | 77.4 | 45.6 | 66.2 | 47.7 | 215.9 | 218 | 215.9 | YES
17 | OK | 28 | 29 | 29 | 75 | 46.9 | 4.73 | 50 | 77.4 | 45.6 | 66.3 | 46.6 | 216.8 | 220.6 | 216.8 | YES
18 | OK | 5 | 6 | 6 | 75 | 165.7 | 3.4 | 50 | 77.4 | 45.6 | 69.4 | 47.7 | 215.9 | 218 | 215.9 | YES
19 | OK | 29 | 31 | 31 | 75 | 93.3 | 4.5 | 50 | 77.4 | 45.6 | 66.8 | 46.6 | 216.8 | 220.6 | 216.8 | YES
20 | OK | 6 | 50 | 50 | 75 | 201.4 | 1.17 | 50 | 77.4 | 45.6 | 74.6 | 46.4 | 215.9 | 220.8 | 215.9 | YES
21 | OK | 31 | 38 | 38 | 75 | 142.9 | 3.06 | 50 | 77.4 | 45.6 | 70.2 | 46.4 | 216.5 | 221 | 216.5 | YES
22 | OK | 38 | 39 | 39 | 75 | 166.7 | 2.83 | 50 | 77.4 | 45.6 | 70.7 | 46.4 | 216.4 | 221 | 216.4 | YES
23 | OK | 39 | 36 | 36 | 75 | 171.8 | 2.63 | 50 | 77.4 | 45.6 | 71.2 | 46.3 | 216.4 | 221.3 | 216.4 | YES
24 | OK | 36 | 37 | 37 | 75 | 192.8 | 2.45 | 50 | 77.4 | 45.6 | 71.6 | 46.3 | 216.4 | 221.3 | 216.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 56-014225
TR_B (available) | 30-004006
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 77.4
TR_B Baseline Loading% | 45.6
Total Scenarios Evaluated | 27
Feasible Scenarios | 24
--- Optimal Solution ---
Switch Parent Node | 25
Switch Child Node | 19
Tie Node (TR_A side) | 17
Tie Node (TR_B side) | 71
Tie Line Distance (m) | 146.5
Load Transferred (kW) | 2.41
TR_A Loading After (%) | 71.7
TR_B Loading After (%) | 47.3
Minimum Voltage (V) | 217.2