## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 14 | 2 | 32 | 9 | 154.9 | 10.9 | 50 | 77.4 | 42.5 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 2 | 1 | 32 | 9 | 154.9 | 7.21 | 50 | 77.4 | 42.5 | 60.6 | 72.2 | 218.2 | 199.9 | 199.9 | NO
| NG | 1 | 3 | 32 | 9 | 154.9 | 6.21 | 50 | 77.4 | 42.5 | 62.9 | 67.7 | 218.2 | 204.1 | 204.1 | NO
| NG | 3 | 4 | 32 | 9 | 154.9 | 5.24 | 50 | 77.4 | 42.5 | 65.1 | 63.5 | 217.8 | 207.6 | 207.6 | NO
| NG | 4 | 0 | 32 | 9 | 154.9 | 4.83 | 50 | 77.4 | 42.5 | 66.1 | 61.8 | 217.8 | 209 | 209 | NO
| NG | 0 | 27 | 32 | 9 | 154.9 | 4.75 | 50 | 77.4 | 42.5 | 66.3 | 61.5 | 217.8 | 209.2 | 209.2 | NO
1 | OK | 27 | 32 | 32 | 9 | 154.9 | 2.14 | 50 | 77.4 | 42.5 | 72.3 | 50.8 | 217.2 | 216.7 | 216.7 | YES
2 | OK | 27 | 33 | 33 | 9 | 221.2 | 2.61 | 50 | 77.4 | 42.5 | 71.3 | 44.2 | 216.7 | 218.2 | 216.7 | YES
3 | ** OPTIMAL ** | 32 | 54 | 54 | 9 | 195.4 | 2.13 | 50 | 77.4 | 42.5 | 72.3 | 50.8 | 217.2 | 216.9 | 216.9 | YES
4 | OK | 32 | 55 | 55 | 9 | 155.7 | 0.01 | 50 | 77.4 | 42.5 | 77.4 | 42.5 | 215.9 | 218.6 | 215.9 | YES
5 | OK | 33 | 44 | 44 | 9 | 223.6 | 1.47 | 50 | 77.4 | 42.5 | 74 | 44.2 | 215.5 | 218.2 | 215.5 | YES
6 | OK | 33 | 58 | 58 | 9 | 235.8 | 1.14 | 50 | 77.4 | 42.5 | 74.7 | 46.9 | 216.7 | 217.7 | 216.7 | YES
7 | OK | 23 | 12 | 13 | 3 | 277.8 | 5.4 | 50 | 77.4 | 42.5 | 64.7 | 49.8 | 216.8 | 213.5 | 213.5 | YES
8 | OK | 12 | 13 | 13 | 3 | 277.8 | 4.73 | 50 | 77.4 | 42.5 | 66.3 | 47.9 | 216.8 | 214.7 | 214.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 56-014225
TR_B (available) | 60-022631
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 77.4
TR_B Baseline Loading% | 42.5
Total Scenarios Evaluated | 14
Feasible Scenarios | 8
--- Optimal Solution ---
Switch Parent Node | 32
Switch Child Node | 54
Tie Node (TR_A side) | 54
Tie Node (TR_B side) | 9
Tie Line Distance (m) | 195.4
Load Transferred (kW) | 2.13
TR_A Loading After (%) | 72.3
TR_B Loading After (%) | 50.8
Minimum Voltage (V) | 216.9