## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 43 | 45 | 47 | 21 | 76.2 | 1.64 | 50 | 36.4 | 35.8 | 35.3 | 35.8 | 218.6 | 222.9 | 218.6 | YES
| NG | 0 | 1 | 8 | 21 | 73.6 | 11.54 | 50 | 36.4 | 35.8 | 7.8 | 82.5 | 227.8 | 205 | 205 | NO
2 | OK | 0 | 27 | 30 | 21 | 5.1 | 8.68 | 50 | 36.4 | 35.8 | 28.6 | 70.3 | 219.8 | 214.4 | 214.4 | YES
3 | OK | 45 | 46 | 46 | 5 | 154.5 | 1.43 | 50 | 36.4 | 35.8 | 35.3 | 35.8 | 218.6 | 222.9 | 218.6 | YES
4 | OK | 45 | 47 | 47 | 21 | 76.2 | 0.21 | 50 | 36.4 | 35.8 | 36.4 | 35.8 | 218.3 | 222.9 | 218.3 | YES
5 | OK | 1 | 2 | 2 | 5 | 85.5 | 2.43 | 50 | 36.4 | 35.8 | 32.4 | 45.2 | 219.2 | 222.4 | 219.2 | YES
| NG | 1 | 3 | 8 | 21 | 73.6 | 9.11 | 50 | 36.4 | 35.8 | 11.8 | 72.6 | 226.9 | 206.6 | 206.6 | NO
6 | OK | 27 | 28 | 30 | 21 | 5.1 | 7.77 | 50 | 36.4 | 35.8 | 29.5 | 66.6 | 219.7 | 215.7 | 215.7 | YES
7 | OK | 47 | 49 | 49 | 23 | 76.5 | 0.21 | 50 | 36.4 | 35.8 | 36.4 | 35.8 | 218.3 | 222.9 | 218.3 | YES
8 | OK | 2 | 4 | 4 | 5 | 127.7 | 1.55 | 50 | 36.4 | 35.8 | 32.4 | 41.8 | 219.2 | 222.4 | 219.2 | YES
| NG | 3 | 7 | 8 | 21 | 73.6 | 8.73 | 50 | 36.4 | 35.8 | 11.8 | 71.1 | 226.9 | 206.6 | 206.6 | NO
9 | OK | 28 | 29 | 30 | 21 | 5.1 | 7.63 | 50 | 36.4 | 35.8 | 29.5 | 66.1 | 219.7 | 215.9 | 215.9 | YES
10 | OK | 4 | 5 | 5 | 5 | 152.7 | 0.73 | 50 | 36.4 | 35.8 | 32.4 | 38.7 | 219.2 | 222.4 | 219.2 | YES
| NG | 7 | 8 | 8 | 21 | 73.6 | 8.2 | 50 | 36.4 | 35.8 | 13.8 | 68.9 | 226.5 | 207.9 | 207.9 | NO
11 | OK | 29 | 30 | 30 | 21 | 5.1 | 7.19 | 50 | 36.4 | 35.8 | 29.5 | 64.3 | 219.7 | 216.8 | 216.8 | YES
12 | OK | 5 | 54 | 54 | 5 | 218.9 | 0.73 | 50 | 36.4 | 35.8 | 33.6 | 38.7 | 219 | 222.4 | 219 | YES
13 | OK | 8 | 11 | 24 | 23 | 74.1 | 1.36 | 50 | 36.4 | 35.8 | 32.9 | 37.7 | 219.5 | 222.9 | 219.5 | YES
| NG | 8 | 14 | 14 | 21 | 82.6 | 6.84 | 50 | 36.4 | 35.8 | 17.2 | 63.3 | 225.7 | 209.9 | 209.9 | NO
14 | OK | 30 | 31 | 31 | 21 | 45.5 | 0.5 | 50 | 36.4 | 35.8 | 34.5 | 37.8 | 218.7 | 221.9 | 218.7 | YES
15 | OK | 30 | 32 | 36 | 23 | 5.8 | 6.69 | 50 | 36.4 | 35.8 | 31.4 | 57.4 | 219.3 | 215.8 | 215.8 | YES
16 | OK | 11 | 23 | 24 | 23 | 74.1 | 0.48 | 50 | 36.4 | 35.8 | 36.4 | 37.7 | 218.3 | 222.9 | 218.3 | YES
| NG | 14 | 15 | 15 | 21 | 122.8 | 6.81 | 50 | 36.4 | 35.8 | 17.2 | 63.2 | 225.7 | 209.9 | 209.9 | NO
17 | OK | 32 | 33 | 36 | 23 | 5.8 | 6.38 | 50 | 36.4 | 35.8 | 31.6 | 56.3 | 219.3 | 216.4 | 216.4 | YES
18 | OK | 15 | 16 | 16 | 21 | 161.6 | 3.7 | 50 | 36.4 | 35.8 | 25.2 | 50.5 | 223.7 | 215.2 | 215.2 | YES
19 | OK | 33 | 35 | 36 | 23 | 5.8 | 5.84 | 50 | 36.4 | 35.8 | 33.6 | 56.3 | 218.8 | 216.4 | 216.4 | YES
20 | OK | 16 | 17 | 17 | 21 | 164.1 | 2.83 | 50 | 36.4 | 35.8 | 25.2 | 47.2 | 223.7 | 215 | 215 | YES
21 | OK | 35 | 36 | 36 | 23 | 5.8 | 4.14 | 50 | 36.4 | 35.8 | 33.6 | 49.3 | 218.8 | 220.1 | 218.8 | YES
22 | OK | 17 | 12 | 9 | 21 | 170.9 | 2.83 | 50 | 36.4 | 35.8 | 25.2 | 47.2 | 223.7 | 215.5 | 215.5 | YES
23 | OK | 36 | 37 | 37 | 23 | 41.1 | 3.42 | 50 | 36.4 | 35.8 | 36.4 | 49.3 | 218.3 | 220.1 | 218.3 | YES
24 | OK | 36 | 41 | 41 | 23 | 42 | 0.72 | 50 | 36.4 | 35.8 | 33.6 | 35.8 | 218.8 | 222.9 | 218.8 | YES
25 | OK | 12 | 13 | 9 | 21 | 170.9 | 1.03 | 50 | 36.4 | 35.8 | 32.3 | 39.9 | 220.2 | 220.4 | 220.2 | YES
26 | OK | 12 | 19 | 19 | 21 | 178.4 | 1.8 | 50 | 36.4 | 35.8 | 29.2 | 43 | 221.7 | 218.4 | 218.4 | YES
27 | OK | 37 | 38 | 38 | 23 | 82.9 | 2.69 | 50 | 36.4 | 35.8 | 36.4 | 46.4 | 218.3 | 221.8 | 218.3 | YES
28 | OK | 41 | 42 | 42 | 23 | 44.6 | 0.2 | 50 | 36.4 | 35.8 | 35.6 | 35.8 | 218.4 | 222.9 | 218.4 | YES
29 | OK | 13 | 18 | 9 | 21 | 170.9 | 0.94 | 50 | 36.4 | 35.8 | 32.3 | 39.6 | 220.2 | 220.7 | 220.2 | YES
30 | ** OPTIMAL ** | 19 | 20 | 21 | 23 | 181.1 | 1.22 | 50 | 36.4 | 35.8 | 31.5 | 40.6 | 220.7 | 222.9 | 220.7 | YES
31 | OK | 38 | 39 | 39 | 23 | 113.3 | 1.58 | 50 | 36.4 | 35.8 | 36.4 | 42 | 218.3 | 223 | 218.3 | YES
32 | OK | 18 | 10 | 9 | 21 | 170.9 | 0.94 | 50 | 36.4 | 35.8 | 32.7 | 39.6 | 220.1 | 220.7 | 220.1 | YES
33 | OK | 20 | 21 | 21 | 23 | 181.1 | 0.56 | 50 | 36.4 | 35.8 | 34.2 | 38 | 219.4 | 222.9 | 219.4 | YES
34 | OK | 39 | 26 | 26 | 23 | 148.3 | 1.2 | 50 | 36.4 | 35.8 | 36.4 | 40.5 | 218.3 | 222.9 | 218.3 | YES
| NG | 10 | 9 | 9 | 21 | 170.9 | 0.94 | 50 | 36.4 | 35.8 | 32.7 |  | 220.1 | 5.1681e+58 | 220.1 | NO
35 | OK | 26 | 25 | 25 | 23 | 170.2 | 0.76 | 50 | 36.4 | 35.8 | 36.4 | 38.8 | 218.3 | 222.9 | 218.3 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 57-000299
TR_B (available) | 66-012661
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 36.4
TR_B Baseline Loading% | 35.8
Total Scenarios Evaluated | 42
Feasible Scenarios | 35
--- Optimal Solution ---
Switch Parent Node | 19
Switch Child Node | 20
Tie Node (TR_A side) | 21
Tie Node (TR_B side) | 23
Tie Line Distance (m) | 181.1
Load Transferred (kW) | 1.22
TR_A Loading After (%) | 31.5
TR_B Loading After (%) | 40.6
Minimum Voltage (V) | 220.7