## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 38 | 39 | 123 | 69 | 89.6 | 17.56 | 50 | 77.8 | 50.5 | [5 empty] | NO | TR_B sim: not converged
| NG | 39 | 40 | 123 | 69 | 89.6 | 16.02 | 50 | 77.8 | 50.5 | [5 empty] | NO | TR_B sim: not converged
| NG | 40 | 3 | 123 | 69 | 89.6 | 15.89 | 50 | 77.8 | 50.5 | [5 empty] | NO | TR_B sim: not converged
| NG | 3 | 2 | 123 | 69 | 89.6 | 15.41 | 50 | 77.8 | 50.5 | [5 empty] | NO | TR_B sim: not converged
| NG | 2 | 4 | 123 | 69 | 89.6 | 15.29 | 50 | 77.8 | 50.5 | [5 empty] | NO | TR_B sim: not converged
| NG | 4 | 1 | 123 | 69 | 89.6 | 14.34 | 50 | 77.8 | 50.5 | [5 empty] | NO | TR_B sim: not converged
| NG | 1 | 0 | 123 | 69 | 89.6 | 13.4 | 50 | 77.8 | 50.5 | [5 empty] | NO | TR_B sim: not converged
| NG | 0 | 26 | 123 | 69 | 89.6 | 12.09 | 50 | 77.8 | 50.5 | 63.2 | 73.7 | 214.9 | 131.6 | 131.6 | NO
| NG | 26 | 25 | 123 | 69 | 89.6 | 10.21 | 50 | 77.8 | 50.5 | 65.5 | 67.2 | 214.4 | 158.7 | 158.7 | NO
| NG | 25 | 42 | 123 | 69 | 89.6 | 9.52 | 50 | 77.8 | 50.5 | 66.3 | 65.5 | 214.4 | 165.7 | 165.7 | NO
| NG | 42 | 43 | 123 | 69 | 89.6 | 8.2 | 50 | 77.8 | 50.5 | 67.9 | 62.7 | 214.4 | 176.9 | 176.9 | NO
| NG | 43 | 124 | 123 | 69 | 89.6 | 7.36 | 50 | 77.8 | 50.5 | 68.9 | 61.1 | 214.4 | 183.1 | 183.1 | NO
| NG | 124 | 125 | 123 | 69 | 89.6 | 6.89 | 50 | 77.8 | 50.5 | 69.4 | 60.3 | 214.3 | 186.3 | 186.3 | NO
| NG | 125 | 66 | 123 | 69 | 89.6 | 6.27 | 50 | 77.8 | 50.5 | 70.2 | 59.3 | 214.3 | 190.2 | 190.2 | NO
| NG | 66 | 9 | 123 | 69 | 89.6 | 6.27 | 50 | 77.8 | 50.5 | 70.2 | 59.3 | 214.3 | 190.2 | 190.2 | NO
| NG | 9 | 10 | 123 | 69 | 89.6 | 5.99 | 50 | 77.8 | 50.5 | 70.5 | 58.8 | 214.2 | 191.8 | 191.8 | NO
| NG | 10 | 41 | 123 | 69 | 89.6 | 5.61 | 50 | 77.8 | 50.5 | 71 | 58.2 | 214.3 | 193.8 | 193.8 | NO
| NG | 41 | 44 | 123 | 69 | 89.6 | 4.64 | 50 | 77.8 | 50.5 | 71.8 | 56.7 | 214.1 | 198.7 | 198.7 | NO
1 | OK | 44 | 64 | 123 | 69 | 89.6 | 3.16 | 50 | 77.8 | 50.5 | 73.9 | 53.2 | 214.1 | 210.7 | 210.7 | YES
2 | OK | 64 | 122 | 123 | 69 | 89.6 | 2.12 | 50 | 77.8 | 50.5 | 75.1 | 53.2 | 214.1 | 210.7 | 210.7 | YES
3 | OK | 122 | 76 | 123 | 69 | 89.6 | 1.54 | 50 | 77.8 | 50.5 | 75.8 | 52.4 | 214.1 | 213 | 213 | YES
4 | OK | 76 | 68 | 123 | 69 | 89.6 | 1.54 | 50 | 77.8 | 50.5 | 75.8 | 52.4 | 214.1 | 213 | 213 | YES
5 | OK | 68 | 69 | 123 | 69 | 89.6 | 0.76 | 50 | 77.8 | 50.5 | 76.8 | 51.4 | 214.1 | 215.9 | 214.1 | YES
6 | ** OPTIMAL ** | 69 | 79 | 123 | 69 | 89.6 | 0.68 | 50 | 77.8 | 50.5 | 76.8 | 51.3 | 214.1 | 216.1 | 214.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 57-002173
TR_B (available) | 35-010218
TR_A Rated kVA | 100
TR_B Rated kVA | 100
TR_A Baseline Loading% | 77.8
TR_B Baseline Loading% | 50.5
Total Scenarios Evaluated | 24
Feasible Scenarios | 6
--- Optimal Solution ---
Switch Parent Node | 69
Switch Child Node | 79
Tie Node (TR_A side) | 123
Tie Node (TR_B side) | 69
Tie Line Distance (m) | 89.6
Load Transferred (kW) | 0.68
TR_A Loading After (%) | 76.8
TR_B Loading After (%) | 51.3
Minimum Voltage (V) | 214.1