## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 31 | 30 | 30 | 24 | 70.4 | 35.71 | 50 | 77.8 | 23.6 | 35.6 | 67.6 | 217 | 207.3 | 207.3 | NO
1 | OK | 31 | 95 | 95 | 19 | 129.4 | 0.26 | 50 | 77.8 | 23.6 | 77.5 | 23.6 | 212.5 | 225.5 | 212.5 | YES
| NG | 31 | 72 | 65 | 24 | 14.2 | 30.03 | 50 | 77.8 | 23.6 | 42.1 | 59.8 | 214 | 209.5 | 209.5 | NO
| NG | 30 | 29 | 29 | 24 | 80 | 34.32 | 50 | 77.8 | 23.6 | 35.6 | 65.9 | 217 | 206.9 | 206.9 | NO
| NG | 72 | 52 | 65 | 24 | 14.2 | 30.03 | 50 | 77.8 | 23.6 | 42.1 | 59.7 | 214 | 209.6 | 209.6 | NO
| NG | 29 | 28 | 28 | 24 | 83.6 | 34.19 | 50 | 77.8 | 23.6 | 37.4 | 65.7 | 216.6 | 207 | 207 | NO
| NG | 52 | 53 | 65 | 24 | 14.2 | 29.96 | 50 | 77.8 | 23.6 | 42.2 | 59.7 | 214 | 209.6 | 209.6 | NO
| NG | 28 | 27 | 27 | 25 | 96.9 | 34.19 | 50 | 77.8 | 23.6 | 37.4 | 65.5 | 216.6 | 208.4 | 208.4 | NO
| NG | 53 | 54 | 65 | 24 | 14.2 | 29.96 | 50 | 77.8 | 23.6 | 42.2 | 59.7 | 214 | 209.6 | 209.6 | NO
| NG | 27 | 34 | 34 | 25 | 102.8 | 34.19 | 50 | 77.8 | 23.6 | 37.4 | 65.5 | 216.6 | 208.4 | 208.4 | NO
| NG | 54 | 55 | 65 | 24 | 14.2 | 29.96 | 50 | 77.8 | 23.6 | 42.2 | 59.7 | 214 | 209.6 | 209.6 | NO
| NG | 34 | 111 | 4 | 24 | 105.5 | 34.19 | 50 | 77.8 | 23.6 | 37.4 | 65.6 | 216.6 | 204.9 | 204.9 | NO
2 | OK | 55 | 56 | 65 | 24 | 14.2 | 29.24 | 50 | 77.8 | 23.6 | 43 | 58.5 | 213.9 | 210.1 | 210.1 | YES
| NG | 111 | 121 | 4 | 24 | 105.5 | 33.68 | 50 | 77.8 | 23.6 | 38 | 65 | 216.5 | 204.7 | 204.7 | NO
3 | OK | 56 | 65 | 65 | 24 | 14.2 | 28.91 | 50 | 77.8 | 23.6 | 43.4 | 58.5 | 213.9 | 210.1 | 210.1 | YES
| NG | 121 | 38 | 4 | 24 | 105.5 | 33.54 | 50 | 77.8 | 23.6 | 38.1 | 64.8 | 216.5 | 204.7 | 204.7 | NO
4 | OK | 65 | 57 | 57 | 24 | 17.7 | 28.91 | 50 | 77.8 | 23.6 | 43.4 | 58.4 | 213.9 | 210.6 | 210.6 | YES
5 | OK | 38 | 39 | 4 | 24 | 105.5 | 17.56 | 50 | 77.8 | 23.6 | 56.8 | 42.8 | 215.5 | 211 | 211 | YES
| NG | 38 | 107 | 107 | 25 | 144.1 | 15.98 | 50 | 77.8 | 23.6 | 58.9 | 18.9 | 213.1 | 6.8 | 6.8 | NO
6 | OK | 57 | 58 | 12 | 27 | 32 | 26.25 | 50 | 77.8 | 23.6 | 46.4 | 38.9 | 213.5 | 217.8 | 213.5 | YES
7 | OK | 39 | 40 | 4 | 24 | 105.5 | 16.02 | 50 | 77.8 | 23.6 | 58.6 | 42.8 | 215.4 | 211 | 211 | YES
8 | OK | 58 | 103 | 12 | 27 | 32 | 26.25 | 50 | 77.8 | 23.6 | 46.4 | 38.9 | 213.5 | 217.8 | 213.5 | YES
9 | OK | 40 | 3 | 4 | 24 | 105.5 | 15.89 | 50 | 77.8 | 23.6 | 58.7 | 42.7 | 215.4 | 210.9 | 210.9 | YES
10 | OK | 103 | 105 | 12 | 27 | 32 | 26.25 | 50 | 77.8 | 23.6 | 46.4 | 38.9 | 213.5 | 217.8 | 213.5 | YES
11 | OK | 3 | 2 | 4 | 24 | 105.5 | 15.41 | 50 | 77.8 | 23.6 | 59.3 | 42.1 | 215.4 | 210.8 | 210.8 | YES
12 | OK | 105 | 106 | 12 | 27 | 32 | 22.73 | 50 | 77.8 | 23.6 | 50.5 | 34.6 | 213.5 | 221.7 | 213.5 | YES
13 | OK | 2 | 4 | 4 | 24 | 105.5 | 15.29 | 50 | 77.8 | 23.6 | 59.4 | 42 | 215.3 | 210.8 | 210.8 | YES
14 | OK | 106 | 104 | 12 | 27 | 32 | 22.28 | 50 | 77.8 | 23.6 | 51 | 34.6 | 213.5 | 221.7 | 213.5 | YES
15 | OK | 4 | 1 | 1 | 24 | 110.2 | 14.34 | 50 | 77.8 | 23.6 | 60.5 | 40.8 | 215.2 | 211.5 | 211.5 | YES
16 | OK | 104 | 73 | 12 | 27 | 32 | 20.3 | 50 | 77.8 | 23.6 | 53.3 | 32.2 | 213.5 | 223 | 213.5 | YES
17 | OK | 1 | 0 | 0 | 24 | 111.3 | 13.4 | 50 | 77.8 | 23.6 | 61.6 | 39.7 | 215.1 | 211.3 | 211.3 | YES
18 | OK | 73 | 67 | 12 | 27 | 32 | 20.24 | 50 | 77.8 | 23.6 | 53.3 | 32.2 | 213.5 | 223 | 213.5 | YES
19 | OK | 0 | 26 | 26 | 24 | 129.7 | 12.09 | 50 | 77.8 | 23.6 | 63.2 | 38.1 | 214.9 | 211.5 | 211.5 | YES
20 | OK | 67 | 21 | 12 | 27 | 32 | 17.93 | 50 | 77.8 | 23.6 | 56.1 | 29.5 | 213.5 | 224.4 | 213.5 | YES
21 | ** OPTIMAL ** | 21 | 22 | 12 | 27 | 32 | 17.93 | 50 | 77.8 | 23.6 | 56.1 | 29.5 | 213.5 | 224.4 | 213.5 | YES
22 | OK | 22 | 23 | 23 | 19 | 51.6 | 2.3 | 50 | 77.8 | 23.6 | 74.8 | 26.3 | 213.1 | 225 | 213.1 | YES
23 | OK | 22 | 85 | 12 | 27 | 32 | 15.63 | 50 | 77.8 | 23.6 | 59.1 | 29.5 | 212.9 | 224.4 | 212.9 | YES
24 | OK | 23 | 20 | 20 | 19 | 91 | 0.96 | 50 | 77.8 | 23.6 | 76.4 | 24.7 | 212.7 | 225.3 | 212.7 | YES
| NG | 85 | 81 | 12 | 27 | 32 | 15.63 | 50 | 77.8 | 23.6 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 23.6% (degenerate)
25 | OK | 81 | 24 | 12 | 27 | 32 | 15.37 | 50 | 77.8 | 23.6 | 59.4 | 29.2 | 212.9 | 224.6 | 212.9 | YES
26 | OK | 24 | 13 | 12 | 27 | 32 | 15.37 | 50 | 77.8 | 23.6 | 59.4 | 29.2 | 212.9 | 224.6 | 212.9 | YES
27 | OK | 13 | 101 | 101 | 27 | 65.8 | 5.84 | 50 | 77.8 | 23.6 | 70.8 | 30.5 | 212.4 | 221.6 | 212.4 | YES
28 | OK | 13 | 110 | 110 | 28 | 34.3 | 9.53 | 50 | 77.8 | 23.6 | 66.3 | 33.4 | 213 | 224.2 | 213 | YES
29 | OK | 101 | 100 | 100 | 27 | 106.1 | 5.48 | 50 | 77.8 | 23.6 | 71.2 | 30.1 | 212.4 | 221.9 | 212.4 | YES
30 | OK | 110 | 74 | 74 | 28 | 34.6 | 7.1 | 50 | 77.8 | 23.6 | 69.2 | 31.9 | 212.7 | 224.6 | 212.7 | YES
31 | OK | 100 | 99 | 99 | 28 | 146.8 | 4.23 | 50 | 77.8 | 23.6 | 72.6 | 28.6 | 212.4 | 223.1 | 212.4 | YES
32 | OK | 74 | 14 | 14 | 28 | 39 | 7.1 | 50 | 77.8 | 23.6 | 69.2 | 31.9 | 212.7 | 224.7 | 212.7 | YES
33 | OK | 14 | 15 | 15 | 28 | 57.9 | 6.13 | 50 | 77.8 | 23.6 | 70.3 | 30.7 | 212.6 | 225.1 | 212.6 | YES
34 | OK | 15 | 7 | 7 | 28 | 62.5 | 6.13 | 50 | 77.8 | 23.6 | 70.3 | 30.1 | 212.6 | 225.2 | 212.6 | YES
35 | OK | 7 | 8 | 8 | 28 | 93.5 | 5.62 | 50 | 77.8 | 23.6 | 70.9 | 30.1 | 212.5 | 225.3 | 212.5 | YES
36 | OK | 8 | 18 | 18 | 28 | 98 | 5.62 | 50 | 77.8 | 23.6 | 70.9 | 29.3 | 212.5 | 225.4 | 212.5 | YES
37 | OK | 18 | 78 | 78 | 28 | 111.2 | 4.9 | 50 | 77.8 | 23.6 | 71.8 | 29.3 | 212.5 | 225.4 | 212.5 | YES
38 | OK | 78 | 120 | 120 | 28 | 131.7 | 0.63 | 50 | 77.8 | 23.6 | 77 | 24.4 | 212.4 | 225.5 | 212.4 | YES
39 | OK | 120 | 16 | 16 | 28 | 147.4 | 0.16 | 50 | 77.8 | 23.6 | 77.6 | 23.8 | 212.4 | 225.5 | 212.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 57-002173
TR_B (available) | 45-010011
TR_A Rated kVA | 100
TR_B Rated kVA | 100
TR_A Baseline Loading% | 77.8
TR_B Baseline Loading% | 23.6
Total Scenarios Evaluated | 54
Feasible Scenarios | 39
--- Optimal Solution ---
Switch Parent Node | 21
Switch Child Node | 22
Tie Node (TR_A side) | 12
Tie Node (TR_B side) | 27
Tie Line Distance (m) | 32
Load Transferred (kW) | 17.93
TR_A Loading After (%) | 56.1
TR_B Loading After (%) | 29.5
Minimum Voltage (V) | 213.5