## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 31 | 30 | 88 | 10 | 33.3 | 35.71 | 50 | 77.8 | 12.7 | 35.6 | 56.4 | 217 | 207.5 | 207.5 | NO
| NG | 30 | 29 | 88 | 10 | 33.3 | 34.32 | 50 | 77.8 | 12.7 | 35.6 | 54.6 | 217 | 206.8 | 206.8 | NO
| NG | 29 | 28 | 88 | 10 | 33.3 | 34.19 | 50 | 77.8 | 12.7 | 37.4 | 54.4 | 216.6 | 207 | 207 | NO
| NG | 28 | 27 | 88 | 10 | 33.3 | 34.19 | 50 | 77.8 | 12.7 | 37.4 | 54.4 | 216.6 | 207 | 207 | NO
| NG | 27 | 34 | 88 | 10 | 33.3 | 34.19 | 50 | 77.8 | 12.7 | 37.4 | 54.4 | 216.6 | 207 | 207 | NO
| NG | 34 | 111 | 88 | 10 | 33.3 | 34.19 | 50 | 77.8 | 12.7 | 37.4 | 54.4 | 216.6 | 207 | 207 | NO
| NG | 111 | 121 | 88 | 10 | 33.3 | 33.68 | 50 | 77.8 | 12.7 | 38 | 53.8 | 216.5 | 206.7 | 206.7 | NO
| NG | 121 | 38 | 88 | 10 | 33.3 | 33.54 | 50 | 77.8 | 12.7 | 38.1 | 53.6 | 216.5 | 206.7 | 206.7 | NO
| NG | 38 | 107 | 88 | 10 | 33.3 | 15.98 | 50 | 77.8 | 12.7 | [5 empty] | NO | TR_B sim: loading 0.1% despite baseline 12.7% (degenerate)
1 | OK | 107 | 108 | 88 | 10 | 33.3 | 15.98 | 50 | 77.8 | 12.7 | 58.9 | 31.5 | 213.1 | 216.5 | 213.1 | YES
2 | OK | 108 | 98 | 88 | 10 | 33.3 | 15.98 | 50 | 77.8 | 12.7 | 58.9 | 29.5 | 213.1 | 217.2 | 213.1 | YES
3 | OK | 98 | 97 | 88 | 10 | 33.3 | 14.29 | 50 | 77.8 | 12.7 | 60.8 | 29.5 | 213.2 | 217.2 | 213.2 | YES
4 | ** OPTIMAL ** | 97 | 62 | 88 | 10 | 33.3 | 13.2 | 50 | 77.8 | 12.7 | 60.8 | 28.3 | 213.2 | 216.8 | 213.2 | YES
5 | OK | 62 | 61 | 88 | 10 | 33.3 | 4.4 | 50 | 77.8 | 12.7 | 72.6 | 17.7 | 213.2 | 226.2 | 213.2 | YES
6 | OK | 61 | 71 | 88 | 10 | 33.3 | 4.4 | 50 | 77.8 | 12.7 | 72.6 | 16.6 | 213.2 | 226.2 | 213.2 | YES
7 | OK | 71 | 70 | 88 | 10 | 33.3 | 4.4 | 50 | 77.8 | 12.7 | 72.6 | 16.6 | 213.2 | 226.2 | 213.2 | YES
8 | OK | 70 | 60 | 88 | 10 | 33.3 | 3.44 | 50 | 77.8 | 12.7 | 73.7 | 16.6 | 212.8 | 226.2 | 212.8 | YES
9 | OK | 60 | 59 | 88 | 10 | 33.3 | 3.44 | 50 | 77.8 | 12.7 | 73.7 | 16.6 | 212.8 | 226.2 | 212.8 | YES
10 | OK | 59 | 37 | 88 | 10 | 33.3 | 3.44 | 50 | 77.8 | 12.7 | 73.7 | 16.6 | 212.8 | 226.2 | 212.8 | YES
11 | OK | 37 | 36 | 88 | 10 | 33.3 | 3.44 | 50 | 77.8 | 12.7 | 73.7 | 16.6 | 212.8 | 226.2 | 212.8 | YES
12 | OK | 36 | 35 | 88 | 10 | 33.3 | 2.74 | 50 | 77.8 | 12.7 | 74.4 | 15.8 | 212.8 | 226.3 | 212.8 | YES
13 | OK | 36 | 45 | 51 | 19 | 100 | 0.7 | 50 | 77.8 | 12.7 | 76.9 | 13.3 | 212.4 | 226.5 | 212.4 | YES
14 | OK | 35 | 75 | 88 | 10 | 33.3 | 2.74 | 50 | 77.8 | 12.7 | 74.5 | 15.8 | 212.8 | 226.3 | 212.8 | YES
15 | OK | 45 | 47 | 47 | 19 | 129.7 | 0.55 | 50 | 77.8 | 12.7 | 77.1 | 13.3 | 212.4 | 226.5 | 212.4 | YES
16 | OK | 45 | 50 | 51 | 19 | 100 | 0.15 | 50 | 77.8 | 12.7 | 77.6 | 12.7 | 212.4 | 226.5 | 212.4 | YES
17 | OK | 75 | 6 | 88 | 10 | 33.3 | 1.95 | 50 | 77.8 | 12.7 | 74.5 | 14.9 | 212.8 | 226.3 | 212.8 | YES
18 | OK | 50 | 51 | 51 | 19 | 100 | 0.15 | 50 | 77.8 | 12.7 | 77.6 | 12.7 | 212.4 | 226.5 | 212.4 | YES
19 | OK | 6 | 5 | 88 | 10 | 33.3 | 1.95 | 50 | 77.8 | 12.7 | 75.5 | 14.9 | 212.3 | 226.3 | 212.3 | YES
20 | OK | 5 | 86 | 88 | 10 | 33.3 | 1.95 | 50 | 77.8 | 12.7 | 75.5 | 14.9 | 212.3 | 226.3 | 212.3 | YES
21 | OK | 86 | 84 | 84 | 19 | 70.6 | 0.23 | 50 | 77.8 | 12.7 | 77.5 | 12.9 | 212.4 | 226.5 | 212.4 | YES
22 | OK | 86 | 89 | 88 | 10 | 33.3 | 1.72 | 50 | 77.8 | 12.7 | 75.7 | 14.7 | 212.3 | 226.3 | 212.3 | YES
23 | OK | 84 | 83 | 83 | 19 | 106.6 | 0.23 | 50 | 77.8 | 12.7 | 77.5 | 12.9 | 212.4 | 226.5 | 212.4 | YES
24 | OK | 89 | 87 | 88 | 10 | 33.3 | 1.72 | 50 | 77.8 | 12.7 | 75.7 | 14.7 | 212.3 | 226.3 | 212.3 | YES
25 | OK | 83 | 63 | 63 | 19 | 110.6 | 0.23 | 50 | 77.8 | 12.7 | 77.5 | 12.9 | 212.4 | 226.5 | 212.4 | YES
26 | OK | 87 | 109 | 88 | 10 | 33.3 | 1.42 | 50 | 77.8 | 12.7 | 76.1 | 14.3 | 212.4 | 226.3 | 212.4 | YES
27 | OK | 109 | 88 | 88 | 10 | 33.3 | 1.42 | 50 | 77.8 | 12.7 | 76.1 | 14.3 | 212.4 | 226.3 | 212.4 | YES
28 | OK | 88 | 80 | 80 | 10 | 33.5 | 1.29 | 50 | 77.8 | 12.7 | 76.2 | 14.2 | 212.4 | 226.4 | 212.4 | YES
29 | OK | 80 | 91 | 114 | 20 | 40.1 | 1.29 | 50 | 77.8 | 12.7 | 76.2 | 14.2 | 212.4 | 225.8 | 212.4 | YES
30 | OK | 91 | 96 | 114 | 20 | 40.1 | 0.56 | 50 | 77.8 | 12.7 | 76.3 | 13.3 | 212.4 | 226 | 212.4 | YES
31 | OK | 96 | 113 | 114 | 20 | 40.1 | 0.56 | 50 | 77.8 | 12.7 | 77.1 | 13.3 | 212.4 | 226 | 212.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 57-002173
TR_B (available) | 58-007247
TR_A Rated kVA | 100
TR_B Rated kVA | 100
TR_A Baseline Loading% | 77.8
TR_B Baseline Loading% | 12.7
Total Scenarios Evaluated | 40
Feasible Scenarios | 31
--- Optimal Solution ---
Switch Parent Node | 97
Switch Child Node | 62
Tie Node (TR_A side) | 88
Tie Node (TR_B side) | 10
Tie Line Distance (m) | 33.3
Load Transferred (kW) | 13.2
TR_A Loading After (%) | 60.8
TR_B Loading After (%) | 28.3
Minimum Voltage (V) | 213.2