## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 31 | 30 | 86 | 7 | 34.5 | 35.71 | 50 | 77.8 | 14.5 | 35.6 | 60 | 217 | 197.2 | 197.2 | NO
1 | OK | 31 | 95 | 95 | 6 | 199.6 | 0.26 | 50 | 77.8 | 14.5 | 77.5 | 14.5 | 212.5 | 224.9 | 212.5 | YES
| NG | 31 | 72 | 52 | 13 | 37.8 | 30.03 | 50 | 77.8 | 14.5 | 42.1 | 50.9 | 214 | 206.2 | 206.2 | NO
| NG | 30 | 29 | 86 | 7 | 34.5 | 34.32 | 50 | 77.8 | 14.5 | 35.6 | 58.1 | 217 | 196.1 | 196.1 | NO
| NG | 72 | 52 | 52 | 13 | 37.8 | 30.03 | 50 | 77.8 | 14.5 | 42.1 | 50.8 | 214 | 206.3 | 206.3 | NO
| NG | 29 | 28 | 86 | 7 | 34.5 | 34.19 | 50 | 77.8 | 14.5 | 37.4 | 57.9 | 216.6 | 196.3 | 196.3 | NO
| NG | 52 | 53 | 56 | 6 | 37.9 | 29.96 | 50 | 77.8 | 14.5 | 42.2 | 50.7 | 214 | 206.7 | 206.7 | NO
| NG | 28 | 27 | 86 | 7 | 34.5 | 34.19 | 50 | 77.8 | 14.5 | 37.4 | 57.9 | 216.6 | 196.3 | 196.3 | NO
| NG | 53 | 54 | 56 | 6 | 37.9 | 29.96 | 50 | 77.8 | 14.5 | 42.2 | 50.7 | 214 | 206.7 | 206.7 | NO
| NG | 27 | 34 | 86 | 7 | 34.5 | 34.19 | 50 | 77.8 | 14.5 | 37.4 | 57.9 | 216.6 | 196.3 | 196.3 | NO
| NG | 54 | 55 | 56 | 6 | 37.9 | 29.96 | 50 | 77.8 | 14.5 | 42.2 | 50.7 | 214 | 206.7 | 206.7 | NO
| NG | 34 | 111 | 86 | 7 | 34.5 | 34.19 | 50 | 77.8 | 14.5 | 37.4 | 57.9 | 216.6 | 196.3 | 196.3 | NO
| NG | 55 | 56 | 56 | 6 | 37.9 | 29.24 | 50 | 77.8 | 14.5 | 43 | 49.5 | 213.9 | 207.3 | 207.3 | NO
| NG | 111 | 121 | 86 | 7 | 34.5 | 33.68 | 50 | 77.8 | 14.5 | 38 | 57.2 | 216.5 | 196 | 196 | NO
| NG | 56 | 65 | 65 | 6 | 38.9 | 28.91 | 50 | 77.8 | 14.5 | 43.4 | 49.4 | 213.9 | 207.9 | 207.9 | NO
| NG | 121 | 38 | 86 | 7 | 34.5 | 33.54 | 50 | 77.8 | 14.5 | 38.1 | 57 | 216.5 | 195.9 | 195.9 | NO
| NG | 65 | 57 | 57 | 6 | 43 | 28.91 | 50 | 77.8 | 14.5 | 43.4 | 49.3 | 213.9 | 208.4 | 208.4 | NO
2 | OK | 38 | 39 | 39 | 10 | 41.8 | 17.56 | 50 | 77.8 | 14.5 | 56.8 | 33.4 | 215.5 | 214.4 | 214.4 | YES
| NG | 38 | 107 | 86 | 7 | 34.5 | 15.98 | 50 | 77.8 | 14.5 | 58.9 | 1414 | 213.1 | 64.7 | 64.7 | NO
| NG | 57 | 58 | 58 | 6 | 59.5 | 26.25 | 50 | 77.8 | 14.5 | 46.4 | 46.1 | 213.5 | 209.4 | 209.4 | NO
3 | ** OPTIMAL ** | 39 | 40 | 40 | 10 | 47.5 | 16.02 | 50 | 77.8 | 14.5 | 58.6 | 33.4 | 215.4 | 214.4 | 214.4 | YES
| NG | 107 | 108 | 86 | 7 | 34.5 | 15.98 | 50 | 77.8 | 14.5 | 58.9 | 33.8 | 213.1 | 209.6 | 209.6 | NO
| NG | 58 | 103 | 103 | 6 | 60.9 | 26.25 | 50 | 77.8 | 14.5 | 46.4 | 46.1 | 213.5 | 209.3 | 209.3 | NO
4 | OK | 40 | 3 | 3 | 11 | 73.1 | 15.89 | 50 | 77.8 | 14.5 | 58.7 | 33.3 | 215.4 | 213.9 | 213.9 | YES
5 | OK | 108 | 98 | 86 | 7 | 34.5 | 15.98 | 50 | 77.8 | 14.5 | 58.9 | 31.7 | 213.1 | 210.5 | 210.5 | YES
| NG | 103 | 105 | 105 | 6 | 64.5 | 26.25 | 50 | 77.8 | 14.5 | 46.4 | 46.1 | 213.5 | 209.4 | 209.4 | NO
6 | OK | 3 | 2 | 2 | 0 | 97.3 | 15.41 | 50 | 77.8 | 14.5 | 59.3 | 32.7 | 215.4 | 213.5 | 213.5 | YES
7 | OK | 98 | 97 | 86 | 7 | 34.5 | 14.29 | 50 | 77.8 | 14.5 | 60.8 | 31.7 | 213.2 | 210.5 | 210.5 | YES
8 | OK | 105 | 106 | 106 | 6 | 92.5 | 22.73 | 50 | 77.8 | 14.5 | 50.5 | 41.7 | 213.5 | 213.7 | 213.5 | YES
9 | OK | 2 | 4 | 4 | 0 | 101.3 | 15.29 | 50 | 77.8 | 14.5 | 59.4 | 32.6 | 215.3 | 213.5 | 213.5 | YES
10 | OK | 97 | 62 | 86 | 7 | 34.5 | 13.2 | 50 | 77.8 | 14.5 | 60.8 | 30.5 | 213.2 | 210 | 210 | YES
11 | OK | 106 | 104 | 104 | 6 | 95.4 | 22.28 | 50 | 77.8 | 14.5 | 51 | 41.2 | 213.5 | 213.6 | 213.5 | YES
12 | OK | 4 | 1 | 1 | 13 | 123.8 | 14.34 | 50 | 77.8 | 14.5 | 60.5 | 31.5 | 215.2 | 212.8 | 212.8 | YES
13 | OK | 62 | 61 | 86 | 7 | 34.5 | 4.4 | 50 | 77.8 | 14.5 | 72.6 | 19.5 | 213.2 | 224.6 | 213.2 | YES
14 | OK | 104 | 73 | 73 | 6 | 129 | 20.3 | 50 | 77.8 | 14.5 | 53.3 | 38.7 | 213.5 | 215.1 | 213.5 | YES
15 | OK | 1 | 0 | 0 | 13 | 126.2 | 13.4 | 50 | 77.8 | 14.5 | 61.6 | 30.4 | 215.1 | 212.6 | 212.6 | YES
16 | OK | 61 | 71 | 86 | 7 | 34.5 | 4.4 | 50 | 77.8 | 14.5 | 72.6 | 18.4 | 213.2 | 224.6 | 213.2 | YES
17 | OK | 73 | 67 | 67 | 6 | 132 | 20.24 | 50 | 77.8 | 14.5 | 53.3 | 38.6 | 213.5 | 215 | 213.5 | YES
18 | OK | 0 | 26 | 26 | 6 | 152.7 | 12.09 | 50 | 77.8 | 14.5 | 63.2 | 28.9 | 214.9 | 212.2 | 212.2 | YES
19 | OK | 71 | 70 | 86 | 7 | 34.5 | 4.4 | 50 | 77.8 | 14.5 | 72.6 | 18.4 | 213.2 | 224.6 | 213.2 | YES
20 | OK | 67 | 21 | 21 | 6 | 145.6 | 17.93 | 50 | 77.8 | 14.5 | 56.1 | 35.8 | 213.5 | 214.2 | 213.5 | YES
21 | OK | 26 | 25 | 25 | 6 | 183 | 10.21 | 50 | 77.8 | 14.5 | 65.5 | 26.7 | 214.4 | 211.9 | 211.9 | YES
22 | OK | 70 | 60 | 86 | 7 | 34.5 | 3.44 | 50 | 77.8 | 14.5 | 73.7 | 18.4 | 212.8 | 224.6 | 212.8 | YES
23 | OK | 21 | 22 | 22 | 6 | 148.4 | 17.93 | 50 | 77.8 | 14.5 | 56.1 | 35.8 | 213.5 | 214.2 | 213.5 | YES
24 | OK | 25 | 42 | 42 | 6 | 212.4 | 9.52 | 50 | 77.8 | 14.5 | 66.3 | 25.9 | 214.4 | 212 | 212 | YES
25 | OK | 60 | 59 | 86 | 7 | 34.5 | 3.44 | 50 | 77.8 | 14.5 | 73.7 | 18.4 | 212.8 | 224.6 | 212.8 | YES
26 | OK | 22 | 23 | 23 | 6 | 153.4 | 2.3 | 50 | 77.8 | 14.5 | 74.8 | 17.1 | 213.1 | 225.1 | 213.1 | YES
27 | OK | 22 | 85 | 85 | 6 | 168.7 | 15.63 | 50 | 77.8 | 14.5 | 59.1 | 33.2 | 212.9 | 214.1 | 212.9 | YES
28 | OK | 59 | 37 | 86 | 7 | 34.5 | 3.44 | 50 | 77.8 | 14.5 | 73.7 | 18.4 | 212.8 | 224.6 | 212.8 | YES
29 | OK | 23 | 20 | 20 | 6 | 174.9 | 0.96 | 50 | 77.8 | 14.5 | 76.4 | 15.6 | 212.7 | 225 | 212.7 | YES
| NG | 85 | 81 | 81 | 6 | 178.3 | 15.63 | 50 | 77.8 | 14.5 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 14.5% (degenerate)
30 | OK | 37 | 36 | 86 | 7 | 34.5 | 3.44 | 50 | 77.8 | 14.5 | 73.7 | 18.4 | 212.8 | 224.6 | 212.8 | YES
31 | OK | 81 | 24 | 24 | 6 | 182.7 | 15.37 | 50 | 77.8 | 14.5 | 59.4 | 32.9 | 212.9 | 214 | 212.9 | YES
32 | OK | 36 | 35 | 86 | 7 | 34.5 | 2.74 | 50 | 77.8 | 14.5 | 74.4 | 17.6 | 212.8 | 224.7 | 212.8 | YES
33 | OK | 36 | 45 | 51 | 30 | 47.4 | 0.7 | 50 | 77.8 | 14.5 | 76.9 | 15.1 | 212.4 | 224.9 | 212.4 | YES
34 | OK | 24 | 13 | 12 | 6 | 203.9 | 15.37 | 50 | 77.8 | 14.5 | 59.4 | 20.1 | 212.9 | 219.7 | 212.9 | YES
35 | OK | 35 | 75 | 86 | 7 | 34.5 | 2.74 | 50 | 77.8 | 14.5 | 74.5 | 17.6 | 212.8 | 224.7 | 212.8 | YES
36 | OK | 45 | 47 | 47 | 19 | 47.8 | 0.55 | 50 | 77.8 | 14.5 | 77.1 | 15.1 | 212.4 | 224.9 | 212.4 | YES
37 | OK | 45 | 50 | 51 | 30 | 47.4 | 0.15 | 50 | 77.8 | 14.5 | 77.6 | 14.5 | 212.4 | 224.9 | 212.4 | YES
38 | OK | 13 | 101 | 101 | 6 | 215.4 | 5.84 | 50 | 77.8 | 14.5 | 70.8 | 21.5 | 212.4 | 217.3 | 212.4 | YES
39 | OK | 13 | 110 | 110 | 6 | 211.8 | 9.53 | 50 | 77.8 | 14.5 | 66.3 | 24.4 | 213 | 218.7 | 213 | YES
40 | OK | 75 | 6 | 86 | 7 | 34.5 | 1.95 | 50 | 77.8 | 14.5 | 74.5 | 16.7 | 212.8 | 224.7 | 212.8 | YES
41 | OK | 50 | 51 | 51 | 30 | 47.4 | 0.15 | 50 | 77.8 | 14.5 | 77.6 | 14.5 | 212.4 | 224.9 | 212.4 | YES
42 | OK | 101 | 100 | 100 | 6 | 234.2 | 5.48 | 50 | 77.8 | 14.5 | 71.2 | 21 | 212.4 | 218.5 | 212.4 | YES
43 | OK | 110 | 74 | 74 | 6 | 219.5 | 7.1 | 50 | 77.8 | 14.5 | 69.2 | 22.8 | 212.7 | 219.2 | 212.7 | YES
44 | OK | 6 | 5 | 86 | 7 | 34.5 | 1.95 | 50 | 77.8 | 14.5 | 75.5 | 16.7 | 212.3 | 224.7 | 212.3 | YES
45 | OK | 74 | 14 | 14 | 6 | 232.4 | 7.1 | 50 | 77.8 | 14.5 | 69.2 | 22.8 | 212.7 | 219.2 | 212.7 | YES
46 | OK | 5 | 86 | 86 | 7 | 34.5 | 1.95 | 50 | 77.8 | 14.5 | 75.5 | 16.7 | 212.3 | 224.7 | 212.3 | YES
47 | OK | 86 | 84 | 84 | 7 | 64.7 | 0.23 | 50 | 77.8 | 14.5 | 77.5 | 14.7 | 212.4 | 224.9 | 212.4 | YES
48 | OK | 86 | 89 | 89 | 7 | 35.8 | 1.72 | 50 | 77.8 | 14.5 | 75.7 | 16.4 | 212.3 | 224.7 | 212.3 | YES
49 | OK | 84 | 83 | 83 | 8 | 93.8 | 0.23 | 50 | 77.8 | 14.5 | 77.5 | 14.7 | 212.4 | 224.9 | 212.4 | YES
50 | OK | 89 | 87 | 87 | 7 | 59.9 | 1.72 | 50 | 77.8 | 14.5 | 75.7 | 16.4 | 212.3 | 224.7 | 212.3 | YES
51 | OK | 83 | 63 | 63 | 8 | 96.8 | 0.23 | 50 | 77.8 | 14.5 | 77.5 | 14.7 | 212.4 | 224.9 | 212.4 | YES
52 | OK | 87 | 109 | 109 | 7 | 66.6 | 1.42 | 50 | 77.8 | 14.5 | 76.1 | 16.1 | 212.4 | 224.7 | 212.4 | YES
53 | OK | 63 | 33 | 33 | 30 | 132.4 | 0.23 | 50 | 77.8 | 14.5 | 77.5 | 14.7 | 212.4 | 224.9 | 212.4 | YES
54 | OK | 109 | 88 | 88 | 7 | 90.7 | 1.42 | 50 | 77.8 | 14.5 | 76.1 | 16.1 | 212.4 | 224.7 | 212.4 | YES
55 | OK | 88 | 80 | 80 | 7 | 92.9 | 1.29 | 50 | 77.8 | 14.5 | 76.2 | 15.9 | 212.4 | 224.7 | 212.4 | YES
56 | OK | 80 | 91 | 91 | 7 | 132 | 1.29 | 50 | 77.8 | 14.5 | 76.2 | 15.9 | 212.4 | 224.7 | 212.4 | YES
57 | OK | 91 | 96 | 96 | 7 | 134.1 | 0.56 | 50 | 77.8 | 14.5 | 76.3 | 15.1 | 212.4 | 224.8 | 212.4 | YES
58 | OK | 96 | 113 | 113 | 7 | 215.2 | 0.56 | 50 | 77.8 | 14.5 | 77.1 | 15.1 | 212.4 | 224.8 | 212.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 57-002173
TR_B (available) | 59-020637
TR_A Rated kVA | 100
TR_B Rated kVA | 100
TR_A Baseline Loading% | 77.8
TR_B Baseline Loading% | 14.5
Total Scenarios Evaluated | 80
Feasible Scenarios | 58
--- Optimal Solution ---
Switch Parent Node | 39
Switch Child Node | 40
Tie Node (TR_A side) | 40
Tie Node (TR_B side) | 10
Tie Line Distance (m) | 47.5
Load Transferred (kW) | 16.02
TR_A Loading After (%) | 58.6
TR_B Loading After (%) | 33.4
Minimum Voltage (V) | 214.4