## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 93 | 48 | 4 | 10 | 5.4 | 64.5 | 50 | 33.1 | 9.8 | [5 empty] | NO | TR_A sim: ไม่พบ load meters: SUBTYPECODE=1 (point) หลังจากกรอง XF
| NG | 48 | 47 | 4 | 10 | 5.4 | 26.99 | 50 | 33.1 | 9.8 | 10.3 | 19.5 | 219.8 | 5 | 5 | NO
1 | OK | 48 | 86 | 89 | 10 | 6.9 | 2.82 | 50 | 33.1 | 9.8 | 31.8 | 9.8 | 214.7 | 220.4 | 214.7 | YES
| NG | 47 | 50 | 4 | 10 | 5.4 | 26.99 | 50 | 33.1 | 9.8 | 10.3 | 19.5 | 219.8 | 5 | 5 | NO
2 | OK | 86 | 90 | 89 | 10 | 6.9 | 1.86 | 50 | 33.1 | 9.8 | 33 | 9.8 | 214.1 | 220.4 | 214.1 | YES
| NG | 50 | 32 | 4 | 10 | 5.4 | 26.99 | 50 | 33.1 | 9.8 | 10.3 | 19.5 | 219.8 | 5 | 5 | NO
3 | OK | 90 | 87 | 89 | 10 | 6.9 | 1.86 | 50 | 33.1 | 9.8 | 33 | 9.8 | 214.1 | 220.4 | 214.1 | YES
| NG | 32 | 31 | 4 | 10 | 5.4 | 22.74 | 50 | 33.1 | 9.8 | 14 | 17.6 | 219 | 205.2 | 205.2 | NO
4 | OK | 87 | 88 | 88 | 73 | 56 | 0.05 | 50 | 33.1 | 9.8 | 33 | 9.8 | 214.1 | 220.4 | 214.1 | YES
5 | OK | 87 | 89 | 89 | 10 | 6.9 | 1.81 | 50 | 33.1 | 9.8 | 33.1 | 9.8 | 214.1 | 220.4 | 214.1 | YES
| NG | 31 | 30 | 4 | 10 | 5.4 | 21.26 | 50 | 33.1 | 9.8 | 15 | 17.1 | 218.8 | 206.4 | 206.4 | NO
| NG | 30 | 29 | 4 | 10 | 5.4 | 21.26 | 50 | 33.1 | 9.8 | 16.1 | 17.1 | 218.6 | 206.4 | 206.4 | NO
| NG | 29 | 28 | 4 | 10 | 5.4 | 20.07 | 50 | 33.1 | 9.8 | 16.1 | 17.1 | 218.6 | 206.4 | 206.4 | NO
6 | OK | 28 | 27 | 4 | 10 | 5.4 | 17.18 | 50 | 33.1 | 9.8 | 19.5 | 15.5 | 217.9 | 210.7 | 210.7 | YES
7 | OK | 28 | 75 | 75 | 10 | 93.1 | 2.89 | 50 | 33.1 | 9.8 | 29.5 | 11.2 | 215.8 | 219.4 | 215.8 | YES
8 | OK | 27 | 58 | 4 | 10 | 5.4 | 7.54 | 50 | 33.1 | 9.8 | 31.2 | 10.5 | 215.4 | 220.2 | 215.4 | YES
9 | OK | 27 | 60 | 60 | 11 | 52.8 | 9.64 | 50 | 33.1 | 9.8 | 21.3 | 14.7 | 217.5 | 212.2 | 212.2 | YES
10 | ** OPTIMAL ** | 75 | 76 | 76 | 10 | 104.5 | 2.89 | 50 | 33.1 | 9.8 | 29.5 | 11.2 | 215.8 | 219.6 | 215.8 | YES
11 | OK | 58 | 36 | 37 | 10 | 34.7 | 7.53 | 50 | 33.1 | 9.8 | 31.2 | 10.5 | 215.4 | 220.2 | 215.4 | YES
12 | OK | 58 | 5 | 4 | 10 | 5.4 | 0.01 | 50 | 33.1 | 9.8 | 33.1 | 9.8 | 214.1 | 220.4 | 214.1 | YES
13 | OK | 60 | 61 | 62 | 73 | 53.4 | 0.89 | 50 | 33.1 | 9.8 | 31.9 | 10.2 | 215 | 220.3 | 215 | YES
14 | OK | 76 | 77 | 77 | 10 | 119.2 | 2.42 | 50 | 33.1 | 9.8 | 30.1 | 11 | 215.6 | 220.1 | 215.6 | YES
15 | OK | 36 | 37 | 37 | 10 | 34.7 | 7.53 | 50 | 33.1 | 9.8 | 31.2 | 10.5 | 215.4 | 220.2 | 215.4 | YES
16 | OK | 77 | 79 | 79 | 10 | 120.9 | 0.64 | 50 | 33.1 | 9.8 | 32.3 | 10.1 | 214.6 | 220.3 | 214.6 | YES
17 | OK | 37 | 38 | 38 | 10 | 50.7 | 5.36 | 50 | 33.1 | 9.8 | 31.2 | 10.5 | 215.4 | 220.2 | 215.4 | YES
18 | OK | 79 | 81 | 81 | 10 | 137.1 | 0.64 | 50 | 33.1 | 9.8 | 32.3 | 10.1 | 214.6 | 220.3 | 214.6 | YES
19 | OK | 38 | 39 | 39 | 10 | 60.4 | 3.52 | 50 | 33.1 | 9.8 | 31.2 | 10.5 | 215.4 | 220.2 | 215.4 | YES
20 | OK | 39 | 59 | 59 | 10 | 70.1 | 2.79 | 50 | 33.1 | 9.8 | 31.2 | 10.5 | 215.4 | 220.2 | 215.4 | YES
21 | OK | 59 | 40 | 40 | 10 | 71.9 | 2.32 | 50 | 33.1 | 9.8 | 31.7 | 10.3 | 215.3 | 220.2 | 215.3 | YES
22 | OK | 40 | 41 | 41 | 10 | 92 | 2.25 | 50 | 33.1 | 9.8 | 31.7 | 10.3 | 215.3 | 220.2 | 215.3 | YES
23 | OK | 41 | 42 | 42 | 10 | 118.9 | 1.05 | 50 | 33.1 | 9.8 | 31.7 | 10.3 | 215.3 | 220.2 | 215.3 | YES
24 | OK | 42 | 43 | 43 | 44 | 134.2 | 1.05 | 50 | 33.1 | 9.8 | 31.7 | 10.3 | 215.3 | 220.2 | 215.3 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 57-002201
TR_B (available) | 28-015244
TR_A Rated kVA | 100
TR_B Rated kVA | 250
TR_A Baseline Loading% | 33.1
TR_B Baseline Loading% | 9.8
Total Scenarios Evaluated | 32
Feasible Scenarios | 24
--- Optimal Solution ---
Switch Parent Node | 75
Switch Child Node | 76
Tie Node (TR_A side) | 76
Tie Node (TR_B side) | 10
Tie Line Distance (m) | 104.5
Load Transferred (kW) | 2.89
TR_A Loading After (%) | 29.5
TR_B Loading After (%) | 11.2
Minimum Voltage (V) | 215.8