## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 63 | 64 | 68 | 33 | 137.2 | 3.8 | 50 | 33.1 | 68.6 | 33.1 | 77.5 | 214.1 | 222 | 214.1 | YES
2 | OK | 64 | 69 | 68 | 33 | 137.2 | 3.8 | 50 | 33.1 | 68.6 | 33.1 | 76.2 | 214.1 | 222.9 | 214.1 | YES
3 | OK | 69 | 65 | 68 | 33 | 137.2 | 2.6 | 50 | 33.1 | 68.6 | 33.1 | 74.6 | 214.1 | 223.8 | 214.1 | YES
4 | OK | 65 | 66 | 68 | 33 | 137.2 | 2.16 | 50 | 33.1 | 68.6 | 33.1 | 73.6 | 214.1 | 223.8 | 214.1 | YES
5 | OK | 66 | 70 | 68 | 33 | 137.2 | 0.58 | 50 | 33.1 | 68.6 | 33.1 | 70 | 214.1 | 223.8 | 214.1 | YES
6 | OK | 8 | 9 | 26 | 6 | 50.9 | 2.44 | 50 | 33.1 | 68.6 | 33.1 | 74.3 | 214.1 | 222.5 | 214.1 | YES
7 | OK | 9 | 25 | 26 | 6 | 50.9 | 1.83 | 50 | 33.1 | 68.6 | 33.1 | 72.9 | 214.1 | 223.3 | 214.1 | YES
8 | OK | 25 | 26 | 26 | 6 | 50.9 | 0.37 | 50 | 33.1 | 68.6 | 33.1 | 68.6 | 214.1 | 223.8 | 214.1 | YES
9 | ** OPTIMAL ** | 45 | 54 | 53 | 6 | 43.6 | 4.7 | 50 | 33.1 | 68.6 | 33.1 | 79.7 | 214.1 | 217.4 | 214.1 | YES
10 | OK | 54 | 55 | 53 | 6 | 43.6 | 4.25 | 50 | 33.1 | 68.6 | 33.1 | 78.6 | 214.1 | 218.2 | 214.1 | YES
11 | OK | 55 | 15 | 53 | 6 | 43.6 | 4.01 | 50 | 33.1 | 68.6 | 33.1 | 78.1 | 214.1 | 218.6 | 214.1 | YES
12 | OK | 15 | 16 | 53 | 6 | 43.6 | 2.89 | 50 | 33.1 | 68.6 | 33.1 | 75.4 | 214.1 | 220.4 | 214.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 57-002201
TR_B (available) | 54-009612
TR_A Rated kVA | 100
TR_B Rated kVA | 50
TR_A Baseline Loading% | 33.1
TR_B Baseline Loading% | 68.6
Total Scenarios Evaluated | 12
Feasible Scenarios | 12
--- Optimal Solution ---
Switch Parent Node | 45
Switch Child Node | 54
Tie Node (TR_A side) | 53
Tie Node (TR_B side) | 6
Tie Line Distance (m) | 43.6
Load Transferred (kW) | 4.7
TR_A Loading After (%) | 33.1
TR_B Loading After (%) | 79.7
Minimum Voltage (V) | 214.1