## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 48 | 49 | 68 | 12 | 51.8 | 34.69 | 50 | 33.1 | 17.4 | 22.7 | 49.9 | 216.3 | 194.7 | 194.7 | NO
| NG | 49 | 51 | 68 | 12 | 51.8 | 34.69 | 50 | 33.1 | 17.4 | 22.7 | 49.9 | 216.3 | 194.7 | 194.7 | NO
| NG | 51 | 52 | 68 | 12 | 51.8 | 34.69 | 50 | 33.1 | 17.4 | 22.7 | 49.9 | 216.3 | 194.7 | 194.7 | NO
| NG | 52 | 2 | 68 | 12 | 51.8 | 34.69 | 50 | 33.1 | 17.4 | 22.7 | 49.9 | 216.3 | 194.7 | 194.7 | NO
| NG | 2 | 3 | 68 | 12 | 51.8 | 34.69 | 50 | 33.1 | 17.4 | 22.7 | 49.9 | 216.3 | 194.7 | 194.7 | NO
| NG | 3 | 6 | 68 | 12 | 51.8 | 32.46 | 50 | 33.1 | 17.4 | 23.1 | 48.6 | 216.2 | 194.5 | 194.5 | NO
| NG | 6 | 44 | 68 | 12 | 51.8 | 30.38 | 50 | 33.1 | 17.4 | 25.1 | 47.2 | 215.8 | 194.4 | 194.4 | NO
| NG | 44 | 56 | 68 | 12 | 51.8 | 29.28 | 50 | 33.1 | 17.4 | 25.1 | 45.6 | 215.8 | 196.8 | 196.8 | NO
| NG | 56 | 46 | 68 | 12 | 51.8 | 27.59 | 50 | 33.1 | 17.4 | 25.8 | 44.1 | 215.6 | 199.1 | 199.1 | NO
| NG | 46 | 23 | 68 | 12 | 51.8 | 27.13 | 50 | 33.1 | 17.4 | 26.4 | 44.1 | 215.5 | 199.1 | 199.1 | NO
1 | ** OPTIMAL ** | 46 | 73 | 74 | 10 | 94.3 | 0.46 | 50 | 33.1 | 17.4 | 32.5 | 18 | 214.2 | 227.4 | 214.2 | YES
| NG | 23 | 24 | 68 | 12 | 51.8 | 25.82 | 50 | 33.1 | 17.4 | 26.4 | 42.3 | 215.5 | 201.8 | 201.8 | NO
| NG | 24 | 63 | 68 | 12 | 51.8 | 25.46 | 50 | 33.1 | 17.4 | 26.8 | 42.3 | 215.4 | 201.8 | 201.8 | NO
2 | OK | 63 | 64 | 68 | 12 | 51.8 | 3.8 | 50 | 33.1 | 17.4 | 33.1 | 21.8 | 214.1 | 226.3 | 214.1 | YES
3 | OK | 64 | 69 | 68 | 12 | 51.8 | 3.8 | 50 | 33.1 | 17.4 | 33.1 | 21.2 | 214.1 | 227.1 | 214.1 | YES
4 | OK | 69 | 65 | 68 | 12 | 51.8 | 2.6 | 50 | 33.1 | 17.4 | 33.1 | 20.4 | 214.1 | 227.2 | 214.1 | YES
5 | OK | 65 | 66 | 68 | 12 | 51.8 | 2.16 | 50 | 33.1 | 17.4 | 33.1 | 19.9 | 214.1 | 227.2 | 214.1 | YES
6 | OK | 66 | 70 | 68 | 12 | 51.8 | 0.58 | 50 | 33.1 | 17.4 | 33.1 | 18.1 | 214.1 | 227.4 | 214.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 57-002201
TR_B (available) | 59-020939
TR_A Rated kVA | 100
TR_B Rated kVA | 100
TR_A Baseline Loading% | 33.1
TR_B Baseline Loading% | 17.4
Total Scenarios Evaluated | 18
Feasible Scenarios | 6
--- Optimal Solution ---
Switch Parent Node | 46
Switch Child Node | 73
Tie Node (TR_A side) | 74
Tie Node (TR_B side) | 10
Tie Line Distance (m) | 94.3
Load Transferred (kW) | 0.46
TR_A Loading After (%) | 32.5
TR_B Loading After (%) | 18
Minimum Voltage (V) | 214.2