## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 7 | 14 | 34 | 29 | 1.3 | 7.19 | 50 | 81.5 | 55 | 53.3 | 88.1 | 221.5 | 180.5 | 180.5 | NO
| NG | 14 | 15 | 34 | 29 | 1.3 | 6.32 | 50 | 81.5 | 55 | 55 | 83.5 | 221.5 | 185.4 | 185.4 | NO
| NG | 15 | 22 | 34 | 29 | 1.3 | 6.32 | 50 | 81.5 | 55 | 56.6 | 83.5 | 221.5 | 185.4 | 185.4 | NO
| NG | 22 | 23 | 34 | 29 | 1.3 | 6.32 | 50 | 81.5 | 55 | 56.6 | 83.5 | 221.5 | 185.4 | 185.4 | NO
| NG | 23 | 24 | 34 | 29 | 1.3 | 5.9 | 50 | 81.5 | 55 | 58.2 | 81.3 | 221.5 | 187.7 | 187.7 | NO
| NG | 24 | 10 | 34 | 29 | 1.3 | 5.43 | 50 | 81.5 | 55 | 60.1 | 79 | 221.5 | 190.1 | 190.1 | NO
| NG | 10 | 30 | 34 | 29 | 1.3 | 1.57 | 50 | 81.5 | 55 | 75.2 | 61.4 | 217.9 | 209.5 | 209.5 | NO
1 | ** OPTIMAL ** | 30 | 31 | 34 | 29 | 1.3 | 1.44 | 50 | 81.5 | 55 | 75.8 | 60.9 | 217.7 | 210 | 210 | YES
2 | OK | 31 | 32 | 34 | 29 | 1.3 | 1.44 | 50 | 81.5 | 55 | 75.8 | 60.9 | 217.7 | 210 | 210 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 57-005796
TR_B (available) | 38-017698
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 81.5
TR_B Baseline Loading% | 55
Total Scenarios Evaluated | 9
Feasible Scenarios | 2
--- Optimal Solution ---
Switch Parent Node | 30
Switch Child Node | 31
Tie Node (TR_A side) | 34
Tie Node (TR_B side) | 29
Tie Line Distance (m) | 1.3
Load Transferred (kW) | 1.44
TR_A Loading After (%) | 75.8
TR_B Loading After (%) | 60.9
Minimum Voltage (V) | 210