## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 14 | 16 | 16 | 6 | 15.5 | 0.46 | 50 | 81.5 | 61.4 | 79.7 | 63.1 | 216.1 | 217 | 216.1 | YES
2 | OK | 3 | 27 | 29 | 9 | 58.9 | 1.02 | 50 | 81.5 | 61.4 | 77.6 | 65.3 | 216.3 | 217.3 | 216.3 | YES
3 | OK | 16 | 17 | 17 | 12 | 16.1 | 0.46 | 50 | 81.5 | 61.4 | 79.7 | 63.1 | 216.1 | 217 | 216.1 | YES
4 | OK | 2 | 1 | 1 | 9 | 139.3 | 3.56 | 50 | 81.5 | 61.4 | 67.8 | 71.1 | 216.3 | 217.3 | 216.3 | YES
5 | OK | 27 | 28 | 29 | 9 | 58.9 | 0.68 | 50 | 81.5 | 61.4 | 78.9 | 64 | 216 | 217.3 | 216 | YES
6 | ** OPTIMAL ** | 1 | 18 | 18 | 9 | 141.1 | 2.71 | 50 | 81.5 | 61.4 | 71 | 66.6 | 216.3 | 217.3 | 216.3 | YES
| NG | 24 | 10 | 10 | 5 | 61.7 | 5.43 | 50 | 81.5 | 61.4 | 60.1 | 82.5 | 221.5 | 213 | 213 | NO
7 | OK | 10 | 9 | 9 | 6 | 64.7 | 3.86 | 50 | 81.5 | 61.4 | 66.2 | 76.2 | 221.5 | 214.3 | 214.3 | YES
8 | OK | 10 | 30 | 30 | 5 | 84.1 | 1.57 | 50 | 81.5 | 61.4 | 75.2 | 67.4 | 217.9 | 216.1 | 216.1 | YES
9 | OK | 9 | 11 | 11 | 7 | 66.6 | 2.94 | 50 | 81.5 | 61.4 | 69.8 | 72.7 | 220.8 | 215 | 215 | YES
10 | OK | 30 | 31 | 31 | 5 | 130.5 | 1.44 | 50 | 81.5 | 61.4 | 75.8 | 66.9 | 217.7 | 216.2 | 216.2 | YES
11 | OK | 11 | 35 | 35 | 7 | 67.4 | 2.2 | 50 | 81.5 | 61.4 | 72.7 | 69.8 | 219.7 | 215.6 | 215.6 | YES
12 | OK | 31 | 32 | 32 | 5 | 132.3 | 1.44 | 50 | 81.5 | 61.4 | 75.8 | 66.9 | 217.7 | 216.2 | 216.2 | YES
13 | OK | 35 | 33 | 33 | 14 | 69.1 | 2.2 | 50 | 81.5 | 61.4 | 72.7 | 69.8 | 219.7 | 215.5 | 215.5 | YES
14 | OK | 33 | 19 | 19 | 14 | 69.3 | 2.2 | 50 | 81.5 | 61.4 | 72.7 | 69.8 | 219.7 | 215.5 | 215.5 | YES
15 | OK | 19 | 13 | 13 | 15 | 74.2 | 1.94 | 50 | 81.5 | 61.4 | 73.7 | 68.9 | 219.4 | 215.5 | 215.5 | YES
16 | OK | 13 | 12 | 12 | 18 | 75.3 | 1.12 | 50 | 81.5 | 61.4 | 77 | 65.8 | 217.9 | 216 | 216 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 57-005796
TR_B (available) | 56-004881
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 81.5
TR_B Baseline Loading% | 61.4
Total Scenarios Evaluated | 17
Feasible Scenarios | 16
--- Optimal Solution ---
Switch Parent Node | 1
Switch Child Node | 18
Tie Node (TR_A side) | 18
Tie Node (TR_B side) | 9
Tie Line Distance (m) | 141.1
Load Transferred (kW) | 2.71
TR_A Loading After (%) | 71
TR_B Loading After (%) | 66.6
Minimum Voltage (V) | 216.3