## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 5 | 4 | 0 | 2 | 57.8 | 9.6 | 50 | 81.5 | 21.9 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 5 | 6 | 8 | 10 | 64.6 | 11.49 | 50 | 81.5 | 21.9 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 4 | 21 | 0 | 2 | 57.8 | 8.58 | 50 | 81.5 | 21.9 | 48.5 | 30 | 217.1 | 222.7 | 217.1 | YES
| NG | 6 | 7 | 8 | 10 | 64.6 | 10.96 | 50 | 81.5 | 21.9 | 38.9 | 60.6 | 222.5 | 207.1 | 207.1 | NO
2 | OK | 21 | 20 | 0 | 2 | 57.8 | 7.82 | 50 | 81.5 | 21.9 | 51.4 | 30 | 217.1 | 222.7 | 217.1 | YES
3 | OK | 7 | 14 | 8 | 10 | 64.6 | 7.19 | 50 | 81.5 | 21.9 | 53.3 | 50.5 | 221.5 | 213.5 | 213.5 | YES
4 | OK | 20 | 3 | 0 | 2 | 57.8 | 7.82 | 50 | 81.5 | 21.9 | 51.4 | 30 | 217.1 | 222.7 | 217.1 | YES
5 | OK | 14 | 15 | 8 | 10 | 64.6 | 6.32 | 50 | 81.5 | 21.9 | 55 | 46.9 | 221.5 | 215.5 | 215.5 | YES
6 | OK | 3 | 2 | 0 | 2 | 57.8 | 6.8 | 50 | 81.5 | 21.9 | 55.3 | 26 | 216.3 | 225.4 | 216.3 | YES
7 | OK | 3 | 27 | 28 | 2 | 132.8 | 1.02 | 50 | 81.5 | 21.9 | 77.6 | 25.9 | 216.3 | 225.2 | 216.3 | YES
8 | OK | 15 | 22 | 8 | 10 | 64.6 | 6.32 | 50 | 81.5 | 21.9 | 56.6 | 46.9 | 221.5 | 215.5 | 215.5 | YES
9 | OK | 2 | 1 | 0 | 2 | 57.8 | 3.56 | 50 | 81.5 | 21.9 | 67.8 | 26 | 216.3 | 225.4 | 216.3 | YES
10 | OK | 27 | 28 | 28 | 2 | 132.8 | 0.68 | 50 | 81.5 | 21.9 | 78.9 | 24.5 | 216 | 226.1 | 216 | YES
11 | OK | 22 | 23 | 8 | 10 | 64.6 | 6.32 | 50 | 81.5 | 21.9 | 56.6 | 46.9 | 221.5 | 215.5 | 215.5 | YES
12 | OK | 1 | 18 | 0 | 2 | 57.8 | 2.71 | 50 | 81.5 | 21.9 | 71 | 26 | 216.3 | 225.4 | 216.3 | YES
13 | OK | 23 | 24 | 8 | 10 | 64.6 | 5.9 | 50 | 81.5 | 21.9 | 58.2 | 45.2 | 221.5 | 216.5 | 216.5 | YES
14 | OK | 18 | 0 | 0 | 2 | 57.8 | 1.74 | 50 | 81.5 | 21.9 | 74.8 | 26 | 216.3 | 225.4 | 216.3 | YES
15 | OK | 24 | 10 | 8 | 10 | 64.6 | 5.43 | 50 | 81.5 | 21.9 | 60.1 | 43.3 | 221.5 | 217.6 | 217.6 | YES
16 | ** OPTIMAL ** | 10 | 9 | 8 | 10 | 64.6 | 3.86 | 50 | 81.5 | 21.9 | 66.2 | 36.9 | 221.5 | 221.6 | 221.5 | YES
17 | OK | 9 | 11 | 8 | 10 | 64.6 | 2.94 | 50 | 81.5 | 21.9 | 69.8 | 33.3 | 220.8 | 223.5 | 220.8 | YES
18 | OK | 11 | 35 | 8 | 10 | 64.6 | 2.2 | 50 | 81.5 | 21.9 | 72.7 | 30.4 | 219.7 | 225 | 219.7 | YES
19 | OK | 35 | 33 | 8 | 10 | 64.6 | 2.2 | 50 | 81.5 | 21.9 | 72.7 | 30.4 | 219.7 | 225 | 219.7 | YES
20 | OK | 33 | 19 | 8 | 10 | 64.6 | 2.2 | 50 | 81.5 | 21.9 | 72.7 | 30.4 | 219.7 | 225 | 219.7 | YES
21 | OK | 19 | 13 | 8 | 10 | 64.6 | 1.94 | 50 | 81.5 | 21.9 | 73.7 | 29.4 | 219.4 | 225.4 | 219.4 | YES
22 | OK | 13 | 12 | 8 | 10 | 64.6 | 1.12 | 50 | 81.5 | 21.9 | 77 | 26.2 | 217.9 | 226.8 | 217.9 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 57-005796
TR_B (available) | 63-013656
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 81.5
TR_B Baseline Loading% | 21.9
Total Scenarios Evaluated | 25
Feasible Scenarios | 22
--- Optimal Solution ---
Switch Parent Node | 10
Switch Child Node | 9
Tie Node (TR_A side) | 8
Tie Node (TR_B side) | 10
Tie Line Distance (m) | 64.6
Load Transferred (kW) | 3.86
TR_A Loading After (%) | 66.2
TR_B Loading After (%) | 36.9
Minimum Voltage (V) | 221.5