## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 21 | 13 | 13 | 17 | 140.4 | 14.47 | 50 | 83.3 | 30.4 | 27.4 | 86.8 | 226.5 | 208.4 | 208.4 | NO
| NG | 13 | 12 | 12 | 17 | 158.5 | 14.47 | 50 | 83.3 | 30.4 | 27.4 | 86.9 | 226.5 | 208 | 208 | NO
| NG | 12 | 15 | 15 | 17 | 175.8 | 12.38 | 50 | 83.3 | 30.4 | 35.5 | 78.3 | 225.1 | 209.8 | 209.8 | NO
| NG | 15 | 14 | 14 | 17 | 200.9 | 12.07 | 50 | 83.3 | 30.4 | 36.7 | 77.1 | 224.8 | 209.7 | 209.7 | NO
1 | ** OPTIMAL ** | 14 | 16 | 16 | 17 | 228.6 | 10.6 | 50 | 83.3 | 30.4 | 42.4 | 71.1 | 223.4 | 210.6 | 210.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 57-006798
TR_B (available) | 65-003893
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 83.3
TR_B Baseline Loading% | 30.4
Total Scenarios Evaluated | 5
Feasible Scenarios | 1
--- Optimal Solution ---
Switch Parent Node | 14
Switch Child Node | 16
Tie Node (TR_A side) | 16
Tie Node (TR_B side) | 17
Tie Line Distance (m) | 228.6
Load Transferred (kW) | 10.6
TR_A Loading After (%) | 42.4
TR_B Loading After (%) | 71.1
Minimum Voltage (V) | 210.6